## Commercial
Comparison of Commercial Building Performance Characteristics Between
2015 and 2018 International Energy Conservation Code |  |  |  | Commercial | Commercial
and ASHRAE/IESNA Standard 90.1-2016 |  |  |  | Provisions | Provisions | ASHRAE/IESNA
For Climate Zone 5A |  |  |  | 2015 IECC | 2018 IECC | Standard 90.1-2016
Administration
|  | Scope |  | Regulate design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate design and construction of buildings for effective use and conservation of energy over useful life of each building | Minimum energy-efficient requirements for design, construction and a plan for operation and maintenance; and criteria for determining compliance with these requirements
|  |  |  | Applies to commercial buildings and buildings sites and associated systems and equipment | Applies to commercial buildings and buildings sites and associated systems and equipment | Applies to commercial buildings, portions of buildings, associated systems and equipment and identified equipment that are part of industrial or manufacturing processes
|  | Applicability |  | Chapter 4 applies to buildings & building sites | Chapter 4 applies to buildings & building sites | New buildings and additions to and alterations of existing buildings; replacement of portions of existing buildings
|  |  |  | Chapter 5 controls the alteration, repair, addition and changes of occupancy of existing buildings & structures | Chapter 5 controls the alteration, repair, addition and changes of occupancy of existing buildings & structures
|  |  | Change in space conditioning | Full compliance for non-conditioned or low-energy space to conditioned space | Full compliance for non-conditioned or low-energy space to conditioned space | Full compliance for unconditioned or semiheated space to conditioned space
|  |  | Change of occupancy | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply | Compliance defined in each section
|  |  |  | LPD must comply with change from one lighting area or space type to another area or space type | LPD must comply with change from one lighting area or space type to another area or space type
|  |  | Compliance | Chapter 4 | Chapter 4
|  |  |  | Commercial buildings comply with one of: | Commercial buildings comply with one of: | Modeling will be required when addition to existing building cannot comply by itself. Trade offs will be allowed by modification(s) to existing components of existing building
|  |  |  | 1) Standard 90.1-2013; or | 1) Standard 90.1-2016; or
|  |  |  | 2) Sections C402, C403, C404 and C405 plus C406; or | 2) Sections C402, C403, C404, C405 and C408 plus C406; or
|  |  |  | 3) Using Total Building Performance where proposed energy cost ≤85% of standard reference design building | 3) Using Total Building Performance where proposed energy cost ≤85% energy cost of standard reference design building
| Building Documentation and Closeout Submittal Requirements |  |  |  | Chapter 1
[5 empty] | Construction documents shall specify the documents be provided to owner ≤90 days of receipt of certificate of occupancy | Construction documents shall specify the documents be provided to owner ≤90 days of receipt of certificate of occupancy
Record documents
[5 empty] | Record of completed work | IECC requirement in Section C103.6
Updated mechanical, electrical & control drawings that indicate changes to
Size, type and location of
Components
Equipment
Assemblies
|  |  | Compliance documentation |  | Energy code compliance documentation | IECC requirement in Section C103.6
Supporting calculations
Documentation includes
Energy code edition used for each system
Each fenestration product installed
Interior lighting power compliance path
Envelope insulation compliance path
System compliance calculations for:
Envelope component performance alternative,
Allowable fan horsepower,
Interior lighting power requirement,
Exterior lighting power requirement
|  |  | System operation control |  | Training for those responsible for maintaining and operating equipment | IECC requirement in Section C103.6
Training to include:
1) Review of manuals and permanent certificate
2) Hands-on demonstration of all:
Normal maintenance procedures,
Normal operating modes,
Emergency shutdown & startup procedures.
3) Training completion report
Building Envelope |  |  |  | Climate Zone 5A | Climate Zone 5A | Climate Zone 5A
Roofs - Non Residential
Insulation entirely above deck
|  |  | Assembly maximum | U-0.032 | U-0.032 | U-0.032
|  |  | Insulation minimum R-Value | R-30 ci | R-30 ci | R-30 ci
Metal building
|  |  | Assembly maximum | U-0.035 | U-0.035 | U-0.037
|  |  | Insulation minimum R-Value | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS or
R-25 + R-8 LS
Attic and other
|  |  | Assembly maximum | U-0.027 | U-0.027 | U-0.021
|  |  | Insulation minimum R-Value | R-38 | R-38 | R-49
Roofs - Residential
Insulation entirely above deck
|  |  | Assembly maximum | U-0.032 | U-0.032 | U-0.032
|  |  | Insulation minimum R-Value | R-30 ci | R-30 ci | R-30 ci
Metal building
|  |  | Assembly maximum | U-0.035 | U-0.035 | U-0.037
|  |  | Insulation minimum R-Value | R-19 + R-11 LS | R-19 + R-11 LS | R-19 + R-11 LS or
R-25 + R-8 LS
Attic and other
|  |  | Assembly maximum | U-0.021 | U-0.021 | U-0.021
|  |  | Insulation minimum R-Value | R-49 | R-49 | R-49
Roofs - Semiheated
Insulation entirely above deck
|  |  | Assembly maximum |  |  | U-0.063
|  |  | Insulation minimum R-Value |  |  | R-15 ci
Metal building
|  |  | Assembly maximum |  |  | U-0.082
|  |  | Insulation minimum R-Value |  |  | R-19
Attic and other
|  |  | Assembly Maximum |  |  | U-0.034
|  |  | Insulation Minimum R-Value |  |  | R-30
| Skylight Curbs |  | Insulation | R-5 | R-5 | R-5
Walls, Above Grade - Non Residential
Mass
|  |  | Assembly maximum | U-0.090 | U-0.090 | U-0.090
|  |  | Insulation minimum R-Value | R-11.4 ci | R-11.4 ci | R-11.4 ci
Metal building
|  |  | Assembly maximum | U-0.052 | U-0.052 | U-0.050
|  |  | Insulation minimum R-Value | R-13 + R-13 ci | R-13 + R-13 ci | R-0 + R-19 ci
Metal framed
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.055
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci | R-13 + R-7.5 ci | R-13 + R-10 ci
Wood framed and other
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.051
|  |  | Insulation minimum R-Value | R-13 + R-3.8 ci or | R-13 + R-3.8 ci or | R-13.0 + R-7.5 ci or
|  |  |  | R-20 | R-20 | R-19 + R-5 ci
Walls, Above Grade - Residential
Mass
|  |  | Assembly maximum | U-0.080 | U-0.080 | U-0.080
|  |  | Insulation minimum R-Value | R-13.3 ci | R-13.3 ci | R-13.3 ci
Metal building
|  |  | Assembly maximum | U-0.052 | U-0.052 | U-0.050
|  |  | Insulation minimum R-Value | R-13 + R-13 ci | R-13 + R-13 ci | R-0 + R-19 ci
Metal framed
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.055
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci | R-13 + R-7.5 ci | R-13 + R-10 ci
Wood framed and other
|  |  | Assembly maximum | U-0.064 | U-0.064 | U-0.051
|  |  | Insulation minimum R-Value | R-13 + R-7.5 ci or | R-13 + R-7.5 ci or | R-13 + R-7.5 ci or
|  |  |  | R-20 + R-3.8 ci | R-20 + R-3.8 ci | R-19 + R-5 ci
Walls, Above Grade - Semiheated
Mass
|  |  | Assembly maximum |  |  | U-0.151
|  |  | Insulation minimum R-Value |  |  | R-5.7 ci
Metal building
|  |  | Assembly maximum |  |  | U-0.094
|  |  | Insulation minimum R-Value |  |  | R-0 + R-9.8 ci
Steel framed
|  |  | Assembly maximum |  |  | U-0.084
|  |  | Insulation minimum R-Value |  |  | R-13 + R-3.8 ci
Wood framed and Other
|  |  | Assembly maximum |  |  | U-0.089
|  |  | Insulation minimum R-Value |  |  | R-13
Wall, Below Grade - Non Residential
Below grade wall
|  |  | Assembly maximum | C-0.119 | C-0.119 | C-0.119
|  |  | Insulation minimum R-Value | R-7.5 ci | R-7.5 ci | R-7.5 ci
Wall, Below Grade - Residential
Below grade wall
|  |  | Assembly maximum | C-0.119 | C-0.119 | C-0.092
|  |  | Insulation minimum R-Value | R-7.5 ci | R-7.5 ci | R-10 ci
Wall, Below Grade - Semiheated
Below grade wall
|  |  | Assembly maximum |  |  | C-1.140
|  |  | Insulation minimum R-Value |  |  | NR
Floors - Non Residential
Mass
|  |  | Assembly maximum | U-0.074 | U-0.074 | U-0.057
|  |  | Insulation minimum R-Value | R-10 ci | R-10 ci | R-14.6 ci
|  | Joist / framing |  |  |  | Steel joists
|  |  | Assembly maximum | U-0.033 | U-0.033 | U-0.038
|  |  | Insulation minimum R-Value | R-30 | R-30 | R-30
Wood framed and other
|  |  | Assembly maximum |  |  | U-0.033
|  |  | Insulation minimum R-Value |  |  | R-30
Floors - Residential
Mass
|  |  | Assembly Maximum | U-0.064 | U-0.064 | U-0.051
|  |  | Insulation Minimum R-Value | R-12.5 ci | R-12.5 ci | R-16.7 ci
|  | Joists / framing |  |  |  | Steel joists
|  |  | Assembly maximum | U-0.033 | U-0.033 | U-0.038
|  |  | Insulation minimum R-Value | R-30 | R-30 | R-30
Wood framed and other
|  |  | Assembly maximum |  |  | U-0.033
|  |  | Insulation minimum R-Value |  |  | R-30
Floors - Semiheated
Mass
|  |  | Assembly maximum |  |  | U-0.107
|  |  | Insulation minimum R-Value |  |  | R-6.3 ci
Steel joist
|  |  | Assembly maximum |  |  | U-0.052
|  |  | Insulation minimum R-Value |  |  | R-19
Wood framed and other
|  |  | Assembly maximum |  |  | U-0.051
|  |  | Insulation minimum R-Value |  |  | R-19
Slab-On-Grade Floors - Non Residential
Unheated
|  |  | Assembly maximum | F-0.54 | F-0.54 | F-0.520
|  |  | Insulation minimum R-Value | R-10 for 24" Below | R-10 for 24" Below | R-15 for 24"
Heated
|  |  | Assembly maximum | F-0.65 | F-0.79 | F-0.688
plus F-0.64 full slab
|  |  | Insulation minimum R-Value | R-15 for 36" Below | R-15 for 36" Below | R-20 for 48"
plus R-5 full slab
Slab-On-Grade Floors - Residential
Unheated
|  |  | Assembly maximum | F-0.54 | F-0.54 | F-0.510
|  |  | Insulation minimum R-Value | R-10 for 24" Below | R-10 for 24" Below | R-20 for 24"
Heated
|  |  | Assembly maximum | F-0.65 | F-0.79 | F-0.688
plus F-0.64 full slab
|  |  | Insulation minimum R-Value | R-15 for 36" Below | R-15 for 36" Below | R-20 for 48"
plus R-5 full slab
Slab-On-Grade Floors - Semiheated
Unheated
|  |  | Assembly maximum |  |  | F-0.730
|  |  | Insulation minimum R-Value |  |  | NR
Heated
|  |  | Assembly maximum |  |  | F-0.900
|  |  | Insulation minimum R-Value |  |  | R-10 for 24"
Opaque Doors - Non Residential
|  | Swinging | Assembly Maximum | U-0.37 | U-0.37 | U-0.370
|  | Garage door <14% glazing | Assembly Maximum |  | U-0.31
|  | Non-swinging | Insulation minimum R-Value | R-4.75 | R-4.75 | U-0.310
Opaque Doors - Residential
|  | Swinging | Assembly maximum | U-0.37 | U-0.37 | U-0.370
|  | Garage door <14% glazing | Assembly maximum |  | U-0.31
|  | Non-swinging | Insulation minimum R-Value | R-4.75 | R-4.75 | U-0.310
Opaque Doors - Semiheated
|  | Swinging | Assembly maximum |  |  | U-0.370
|  | Non-swinging | Assembly maximum |  |  | U-0.360
Fenestration - Non Residential
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  | U-0.31
|  |  | Metal framing, fixed |  |  | U-0.38
|  |  | Metal framing, operable |  |  | U-0.46
|  |  | Metal framing, entrance door |  |  | U-0.68
|  |  | Sola Heat Gain Coefficient, all |  |  | SHGC-0.38
|  |  | VT/SHGC, all |  |  | 1.1
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  | U-0.50
|  |  | Assembly maximum |  |  | SHGC-0.40
Fenestration - Residential
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  | U-0.31
|  |  | Metal framing, fixed |  |  | U-0.38
|  |  | Metal framing, operable |  |  | U-0.46
|  |  | Metal framing, entrance door |  |  | U-0.68
|  |  | Sola Heat Gain Coefficient, all |  |  | SHGC-0.38
|  |  | VT/SHGC, all |  |  | 1.1
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  | U-0.50
|  |  | Assembly maximum |  |  | SHGC-0.40
Fenestration - Semiheated
Vertical glazing, 0-40% of wall
|  |  | Nonmetal framing, all |  |  | U-0.45
|  |  | Metal framing, fixed |  |  | U-0.62
|  |  | Metal framing, operable |  |  | U-0.70
|  |  | Metal framing, entrance door |  |  | U-0.77
|  |  | Sola Heat Gain Coefficient, all |  |  | NR
|  |  | VT/SHGC, all |  |  | NR
Skylight, all types, 0-3% of roof
|  |  | Assembly maximum |  |  | U-0.98
|  |  | Assembly maximum |  |  | NR
Fenestration
|  | Vertical | Fixed fenestration | U-0.38 | U-0.38
|  |  | Operable fenestration | U-0.45 | U-0.45
|  |  | Entrance doors | U-0.77 | U-0.77
Solar Heat Gain Coefficient by orientation
|  |  | PF <0.2 | SHGC-0.40 (SEW) | SHGC-0.38 (SEW) | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF
|  |  |  | SHGC-0.53 (N) | SHGC-0.51 (N)
|  |  | 0.2 ≤ PF < 0.5 | SHGC-0.48 (SEW) | SHGC-0.46 (SEW)
|  |  |  | SHGC-0.58 (N) | SHGC-0.56 (N)
|  |  | PF ≥ 0.5 | SHGC-0.64 (SEW) | SHGC-0.61 (SEW)
|  |  |  | SHGC-0.64 (N) | SHGC-0.61 (N)
|  |  | Maximum area (percentage of gross above-grade wall area) | ≤30% | ≤30% | ≤40%
|  |  | Maximum Increased Fenestration Area: | ≤40% When | ≤40% When | ≥40% When vertical fenestration on street side of street-level story only, provided:
|  |  |  | 1) For buildings ≤2 stories; ≥50% net floor area in daylight zone | 1) For buildings ≤2 stories; ≥50% net floor area in daylight zone | a) Street side of street-level story ≤20 ft in height
|  |  |  | 2) For buildings ≥3 stories; ≥25% net floor area in daylight zone | 2) For buildings ≥3 stories; ≥25% net floor area in daylight zone | b) Fenestration has continuous overhang with weighted average PF >0.5
|  |  |  | 3) Daylight responsive lighting controls installed in daylight zone | 3) Daylight responsive lighting controls installed in daylight zone | c) Fenestration area for street side of street-level story <75% gross wall area for street side of street-level story
|  |  |  | 4) Visible Transmittance ≥1.1 times SHGC | 4) Visible Transmittance ≥1.1 times SHGC
|  | Skylights | U-factors | U-0.50 | U-0.50 | U-0.50
|  |  |  | U-0.75 | U-0.75 | U-075
|  |  |  | When daylight responsive controls installed in daylight zone | When daylight responsive controls installed in daylight zone | When haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
|  |  | Solar Heat Gain Coefficient | SHGC-0.40 | SHGC-0.40 | SHGC - 0.40
|  |  |  | SHGC-0.60 | SHGC-0.60 | Except when
|  |  |  | When automated daylighting controls installed in daylight zone | When daylight responsive controls installed above daylight zones | Haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
|  |  | Maximum area (percentage of roof area) | ≤3% | ≤3% | ≤3%
|  |  | Maximum increased skylight area | ≤5% When | ≤6% When | ≤6% When
|  |  |  | Automatic daylighting controls installed in daylight zones under skylights | Daylight responsive controls installed in toplit zones | Total daylight area under skylights ≥50% floor area of space and haze value >90%; skylight VT >0.40; all general lighting in daylight area under skylights controlled by multilevel photocontrols
Insulation of Radiant Heating Systems
|  |  | Insulation on surfaces not facing the heated space |  |  | Radiant floor heating
|  |  | Insulation minimum R-value | R-3.5 | R-3.5 | R-3.5 on bottom surface
Adjacent envelope insulation counts toward requirement
Fenestration Orientation
|  |  | Comply with either |  |  | AW ≤ (AT)/4 and
AE ≤ (AT)/4
AW x SHGCW ≤ (AT x SHGCC)/4 and
AE x SHGCE ≤ (AT x SHGCC)/4
Required Skylights
Required locations
|  |  | Enclosed space | >2,500 sq ft | >2,500 sq ft | ≥2,500 sq ft
|  |  |  | Under roof with ≥75% of ceiling area with ceiling height >15 ft | Under roof with ≥75% of ceiling area with ceiling height >15 ft | Under roof with ceiling heights >15 ft
|  |  | Defined space type | Office, Lobby, Atrium, Concourse, Corridor, Storage space, Gymnasium/exercise center, Convention center, Automotive service area, Space where manufacturing occurs, Nonrefrigerated warehouse, Retail store, Distribution/sorting area, Transportation depot or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage space, Gymnasium/exercise center, Convention center, Automotive service area, Space where manufacturing occurs, Nonrefrigerated warehouse, Retail store, Distribution/sorting area, Transportation depot or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage (including nonrefrigerated warehouse), Gymnasium, Fitness/exercise area, Playing area, Gymnasium seating area, Convention exhibit/event space, Courtroom, Automotive service, Fire station engine room, Manufacturing corridor/transition and bay areas, Retail, Library reading and stack areas, Distribution/sorting area, Transportation baggage and seating areas, or Workshop
Applies To Unconditioned Spaces
|  |  | Minimum skylight fenestration area | Total daylight zone under skylight ≥50% floor area | Total daylight zone under skylight ≥50% floor area | Total daylight zone under skylight ≥50% floor area
|  |  |  | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or
|  |  |  | Skylight effective aperture ≥1% | Skylight effective aperture ≥1% | Skylight effective aperture ≥1%
|  |  |  | Haze value >90% | Haze value >90% | Haze value >90%
|  |  | Lighting controls | Daylight responsive control of all lighting in daylight zone | Daylight responsive control of all lighting in daylight zone | Daylight responsive control of all lighting in daylight zone
|  |  | Exceptions | Space LPD <0.5 w/sf | Space LPD <0.5 w/sf
|  |  |  | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm
|  |  |  | Daylight area under roof monitors >50% enclosed space floor area | Daylight area under roof monitors >50% enclosed space floor area | Daylight area under roof monitors >50% enclosed space floor area
|  |  |  | Spaces where total area minus daylight zone adjacent to vertical fenestration <2,500 sf & when lighting is controlled | Spaces where total area minus daylight zone adjacent to vertical fenestration <2,500 sf & when lighting is controlled | Enclosed spaces where total area minus primary & secondary sidelighted area(s) <2,500 sf and where lighting is controlled to sidelighting requirements
Enclosed space where 90% skylight area shaded on June 21 @ noon by permanent architectural features of building
| Alternate Envelope Compliance Path |  |  | Component Performance Alternative | Component Performance Alternative | Building Envelope Performance Factor Trade-Off
| Rigid Insulation |  |  | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers
Insulation Installation
|  |  | Eave Vent Baffles |  |  | Required with eave vents
|  |  | Substantial contact |  |  | In substantial contact with inside surface in accordance with manufacturers' recommendations for framing system used
|  |  | Recessed HVAC equipment in thermal envelope |  |  | Not recessed in manner as to affect insulation thickness
|  |  | Recessed lighting In thermal envelope |  |  | Not recessed in manner as to affect insulation thickness
Comply with envelope air leakage requirements
|  |  | Extent of insulation |  |  | Over full component area
| Dynamic Glazing |  |  | Ratio of higher to lower labeled SHGC ≥2.4 & automatically controlled to modulate solar gain into space, Can not be used in averaging | Ratio of higher to lower labeled SHGC ≥2.4 & automatically controlled to modulate solar gain into space, Can not be used in averaging | Minimum SHGC used to demonstrate compliance, cannot be used in averaging
Air Leakage
|  | Air barriers |  | Continuous throughout thermal envelope | Continuous throughout thermal envelope | Continuous throughout thermal envelope
|  |  | Air barrier construction | Continuous for all assemblies | Continuous for all assemblies | Continuous for all assemblies
|  |  |  | All joints and seams sealed including transitions in places and changes in materials | All joints and seams sealed including transitions in places and changes in materials | All joints and seams sealed including transitions in places and changes in materials
|  |  |  | All penetrations sealed | All penetrations sealed | All penetrations sealed
|  |  |  | Ability to resist positive and negative pressure | Ability to resist positive and negative pressure | Ability to resist positive and negative pressure
|  |  | Air barrier compliance options | Materials with air permeability ≤0.004 cfm/sf | Materials with air permeability ≤0.004 cfm/sf | Materials with air permeability ≤0.004 cfm/sf
|  |  |  | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf
|  |  |  | Tested air leakage rate of completed building ≤0.40 cfm/sf |  | Tested air leakage rate of completed building ≤0.40 cfm/sf
Air leakage for fenestration
Maximum infiltration rate for fenestration assemblies
|  |  | Windows | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Sliding doors | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Swinging doors | 0.20 cfm/sf | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Skylights - with condensation weepage openings | 0.30 cfm/sf | 0.30 cfm/sf | 0.30 cfm/sf
|  |  | Skylights - all other | 0.20 cfm/sf | 0.20 cfm/sf | 0.50 cfm/sf
|  |  | Curtain wall | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf
|  |  | Storefront glazing | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf
|  |  | Commercial glazed swinging entrance doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf
|  |  | Power-operated sliding doors & power-operated folding doors |  | 1.00 cfm/sf | 1.00 cfm/sf
|  |  | Revolving doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf
|  |  | Garage doors | 0.40 cfm/sf | 0.40 cfm/sf | 0.40 cfm/sf
|  |  | Rolling doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.3 cfm/sf
|  |  | High-speed doors | 1.30 cfm/sf | 1.30 cfm/sf | 1.3 cfm/sf
Rooms containing fuel-burning appliances
|  |  | Ducted combustion air for space conditioning appliances | Appliances and openings located outside thermal envelope or | Appliances and openings located outside thermal envelope or
|  |  |  | Enclosed in room isolated from inside thermal envelope and with ≥R-8 insulation on combustion air duct in conditioned space | In enclosed, isolated & insulated room inside thermal envelope and with ≥R-8 insulation on combustion air duct in conditioned space
Doors and access openings to shafts, chutes, stairways and elevator lobbies
|  |  | From conditioned space | Meet air infiltration requirements if in thermal envelope | Meet air infiltration requirements if in thermal envelope
|  |  | Not in thermal envelope | Be gasketed, weatherstripped or sealed | Be gasketed, weatherstripped or sealed
|  | Air intakes, exhaust openings, stairways and shafts integral to building envelope |  | Provided with dampers | Provided with dampers
|  |  | Stairway and shaft vents | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf
|  |  | Outdoor air intakes and exhausts | Motorized dampers with maximum leakage rate of 4 cfm/sf | Motorized dampers with maximum leakage rate of 4 cfm/sf
|  |  |  | Gravity dampers for defined exceptions | Gravity dampers for defined exceptions
|  | Loading dock weatherseals |  | Yes | Yes | Yes
|  | Building entrance vestibules with self-closing device on doors |  | Space ≥3000 sf without revolving door or air curtain | Space ≥3000 sf without revolving door or air curtain | Vestibule floor area ≤50 sf or 2% of gross conditioned floor area of that level
Exterior envelope of conditioned vestibule meet requirements for conditioned space
Interior & exterior envelope of unconditioned vestibule meet requirements for semiheated space
Building entrance from space ≥1,000 sf without revolving door
Doors opening directly from space ≥3,000 sf and is not separated from building entrance
|  | Recessed lighting In thermal envelope |  | IC-Rated | IC-Rated | Not recessed in manner as to affect insulation thickness
|  |  |  | Labeled air leakage rate ≤2.0 cfm | Labeled air leakage rate ≤2.0 cfm | Comply with envelope air leakage requirements
|  |  |  | Sealed with gasket or caulk between housing and interior covering | Sealed with gasket or caulk between housing and interior covering
Heating, Ventilating and Air Conditioning
| Simplified Approach (ASHRAE), Simple Systems (IECC) |  |  |  |  | ≤2 stories and ≤25,000 sf with compliant single zone HVAC system
Has defined criteria and requirements
| Equipment and System Sizing |  |  | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations
|  |  |  | Loads adjusted to account for energy recovery | Loads adjusted to account for energy recovery
|  |  |  | Heating & cooling equipment capacity ≤ calculated loads | Heating & cooling capacity ≤ smallest available equipment size that exceeds calculated loads
Calculate pressure drop through each device and pipe segment in critical circuit at design conditions
Mechanical Equipment Efficiency
Air Conditioners, Air Cooled
|  | <65,000 Btu/h, split systems |  | 13.0 SEER | 13.0 SEER | 13.0 SEER
|  | <65,000 Btu/h, single package |  | 14.0 SEER | 14.0 SEER | 14.0 SEER
|  | ≤30,000 Btu/h Through-the-wall, air cooled, split system |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | ≤30,000 Btu/h Through-the-wall air cooled single package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.2 EER 12.8 IEER | 11.2 EER 12.8 IEER | 11.2 EER 12.9 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.0 EER 12.6 IEER | 11.0 EER 12.6 IEER | 11.0 EER 12.7 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.0 EER 12.4 IEER | 11.0 EER 12.4 IEER | 11.0 EER 12.4 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 10.8 EER 12.2 IEER | 10.8 EER 12.2 IEER | 10.8 EER 12.2 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 10.0 EER 11.6 IEER | 10.0 EER 11.6 IEER | 10.0 EER 11.6 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 9.8 EER 11.4 IEER | 9.8 EER 11.4 IEER | 9.8 EER 11.4 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 9.7 EER 11.2 IEER | 9.7 EER 11.2 IEER | 9.7 EER 11.2 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 9.5 EER 11.0 IEER | 9.5 EER 11.0 IEER | 9.5 EER 11.0 IEER
|  | <65,000 Btu/h Small-duct high-velocity, air cooled split system |  | 11.0 SEER | 11.0 SEER | 11.0 SEER
Air Conditioner, Water Cooled
|  | <65,000 Btu/h, Split systems and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.1 EER 13.9 IEER | 12.1 EER 13.9 IEER | 12.1 EER 13.9 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.9 EER 13.7 IEER | 11.9 EER 13.7 IEER | 11.9 EER 13.7 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.5 EER 13.9 IEER | 12.5 EER 13.9 IEER | 12.5 EER 13.9 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 12.3 EER 13.7 IEER | 12.3 EER 13.7 IEER | 12.3 EER 13.7 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.4 EER 13.6 IEER | 12.4 EER 13.6 IEER | 12.4 EER 13.6 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 12.2 EER 13.4 IEER | 12.2 EER 13.4 IEER | 12.2 EER 13.4 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.2 EER 13.5 IEER | 12.2 EER 13.5 IEER | 12.2 EER 13.5 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 12.0 EER 13.3 IEER | 12.0 EER 13.3 IEER | 12.0 EER 13.3 IEER
Air Conditioner, Evaporatively Cooled
|  | <65,000 Btu/h, Split systems and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER
|  | ≥240,000 & <760,000 Btu/h, All other heating section, split system and single package |  | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, All other heating section, split system and single package |  | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER
Condensing Units, Air Cooled
|  |  | ≥135,000 Btu/h | 10.5 EER 11.8 IPLV | 10.5 EER 11.8 IPLV | 10.5 EER 11.8 IEER
Condensing Units, Water or Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IEER
Condensing Units, Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IPLV | 13.5 EER 14.0 IEER
Heat Pumps, Electrically Operated, Air Cooled (Cooling Mode)
|  | <65,000 Btu/h, Split systems |  | 14.0 SEER | 14.0 SEER | 14.0 SEER
|  | <65,000 Btu/h, Single package |  | 14.0 SEER | 14.0 SEER | 14.0 SEER
|  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 11.0 EER 12.0 IEER | 11.0 EER 12.0 IEER | 11.0 EER 12.2 IEER
|  | ≥65,000 & <135,000 Btu/h, All other heating section, split system and single package |  | 10.8 EER 11.8 IEER | 10.8 EER 11.8 IEER | 10.8 EER 12.0 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 10.6 EER 11.6 IEER | 10.6 EER 11.6 IEER | 10.6 EER 11.6 IEER
|  | ≥135,000 & <240,000 Btu/h, All other heating section, split system and single package |  | 10.4 EER 11.4 IEER | 10.4 EER 11.4 IEER | 10.4 EER 11.4 IEER
|  | ≥240,000 Btu/h, Electric resistance (or none) heating section, split system and single package |  | 9.5 EER 10.6 IEER | 9.5 EER 10.6 IEER | 9.5 EER 10.6 IEER
|  | ≥240,000 Btu/h, All other heating section, split system and single package |  | 9.3 EER 9.4 IEER | 9.3 EER 9.4 IEER | 9.3 EER 9.4 IEER
|  | ≤30,000 Btu/h Through-the-wall, air cooled split system |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | ≤30,000 Btu/h Through-the-wall, air cooled, single package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | <65,000 Btu/h Small-duct high velocity, split system |  | 11.0 SEER | 11.0 SEER | 11.0 SEER
Heat Pumps, Electrically Operated, Water to Air, 86℉ Entering Water (Cooling Mode)
|  |  | <17,000 Btu/h | 12.2 EER | 12.2 EER | 12.2 EER
|  |  | ≥17,000 & <65,000 Btu/h | 13.0 EER | 13.0 EER | 13.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 13.0 EER | 13.0 EER | 13.0 EER
Heat Pumps, Electrically Operated, Water to Air, Groundwater Source, 59ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 18.0 EER | 18.0 EER | 18.0 EER
Heat Pumps, Electrically Operated, Brine to Air, Ground Loop, 77ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 14.1 EER | 14.1 EER | 14.1 EER
Heat Pumps, Electrically Operated, Water to Water, Water Source, (Cooling Mode)
|  | <135,000 Btu/h, 86° entering water temperature |  | 10.6 EER | 10.6 EER | 10.6 EER
|  | <135,000 Btu/h, 59° entering water temperature |  | 16.3 EER | 16.3 EER | 16.3 EER
Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 77ºF Entering Water (Cooling Mode)
|  |  | <135,000 Btu/h | 12.1 EER | 12.1 EER | 12.1 EER
Heat Pumps, Electrically Operated, Air Cooled (Heating Mode)
|  | <65,000 Btu/h (cooling capacity), split systems |  | 8.2 HSPF | 8.2 HSPF | 8.2 HSPF
|  | <65,000 Btu/h (cooling capacity), single package |  | 8.0 HSPF | 8.0 HSPF | 8.0 HSPF
|  | ≥65,000 & <135,000 Btu/h (cooling capacity), 47ºF db/43ºF wb outdoor air |  | 3.3 COP | 3.3 COP | 3.3 COP
|  | ≥65,000 & <135,000 Btu/h (cooling capacity), 17ºF db/15ºF wb outdoor air |  | 2.25 COP | 2.25 COP | 2.25 COP
|  | ≥135,000 Btu/h (cooling capacity), 47ºF db/43ºF wb outdoor air |  | 3.2 COP | 3.2 COP | 3.2 COP
|  | ≥135,000 Btu/h (cooling capacity), 17ºF db/15ºF wb outdoor air |  | 2.05 COP | 2.05 COP | 2.05 COP
|  | ≤30,000 Btu/h Through-the-Wall, split system |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF
|  | ≤30,000 Btu/h Through-the-Wall, single package |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF
|  | <65,000 Btu/h Small-duct high velocity, split system |  | 6.8 HSPF | 6.8 HSPF | 6.8 HSPF
Heat Pumps, Electrically Operated, Water to Air, Water Loop, 68℉ Entering Water (Heating Mode)
|  | <135,000 Btu/h (cooling capacity) |  | 4.3 COP | 4.3 COP | 4.3 COP
Heat Pumps, Electrically Operated, Water to Air, Groundwater Loop, 50ºF Entering Water (Heating Mode)
|  | <135,000 Btu/h (cooling capacity) |  | 3.7 COP | 3.7 COP | 3.7 COP
Heat Pumps, Electrically Operated, Water to Air, Ground Loop, 32ºF Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.2 COP | 3.2 COP | 3.2 COP
Heat Pumps, Electrically Operated, Water to Water, Water Loop, 68º Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.7 COP | 3.7 COP | 3.7 COP
Heat Pumps, Electrically Operated, Water to Water, Ground Water, 50º Entering Water (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 3.1 COP | 3.1 COP | 3.1 COP
Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 32º Entering Fluid (Heating Mode)
|  |  | <135,000 Btu/h (cooling capacity) | 2.5 COP | 2.5 COP | 2.5 COP
Condensing Units, Air Cooled
|  |  | ≥135,000 Btu/h | 10.1 EER 11.2 IPLV | 10.1 EER 11.2 IPLV | 10.5 EER 11.8 IEER
Condensing Units, Water or Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.1 EER 13.1 IPLV | 13.1 EER 13.1 IPLV | 13.5 EER 14.0 IEER
Electrically Operated Package Terminal and Single Package Vertical Air Conditioners & Heat Pumps
|  | PTAC (cooling mode) new construction (standard size in 90.1) |  | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER
|  | PTAC (cooling mode) replacement (nonstandard size in 90.1) |  | 10.9 - (0.213 x Cap/1000) EER | 10.9 - (0.213 x Cap/1000) EER | 10.9 - (0.213 x Cap/1000) EER
|  | PTHP (cooling mode) new construction (standard size in 90.1) |  | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER
|  | PTHP (cooling mode) replacement (nonstandard size in 90.1) |  | 10.8 - (0.213 x Cap/1000) EER | 10.8 - (0.213 x Cap/1000) EER | 10.8 - (0.213 x Cap/1000) EER
|  | PTHP (heating mode) new construction (standard size in 90.1) |  | 3.2 - (0.026 x Cap/1000) COP | 3.2 - (0.026 x Cap/1000) COP | 3.7 - (0.052 x Cap/1000) COP
|  | PTHP (heating mode) replacement (nonstandard size in 90.1) |  | 2.9 - (0.026 x Cap/1000) COP | 2.9 - (0.026 x Cap/1000) COP | 2.9 - (0.026 x Cap/1000) COP
SPVAC (cooling mode)
|  |  | <65,000 Btu/h | 9.0 EER | 9.0 EER | 10.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 8.9 EER | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 8.6 EER | 10.0 EER
SPVHP (cooling mode)
|  |  | <65,000 Btu/h | 9.0 EER | 9.0 EER | 10.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 8.9 EER | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 8.6 EER | 10.0 EER
SPVHP (heating mode)
|  |  | <65,000 Btu/h | 3.0 COP | 3.0 COP | 3.0 COP
|  |  | ≥65,000 & <135,000 Btu/h | 3.0 COP | 3.0 COP | 3.0 COP
|  |  | ≥135,000 & <240,000 Btu/h | 2.9 COP | 2.9 COP | 3.0 COP
SPVAC (cooling mode), nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  |  | 9.2 EER
|  |  | >30,000 and ≤36,000 Btu/h |  |  | 9.0 EER
SPVHP (cooling mode), nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  |  | 9.2 EER
|  |  | >30,000 and ≤36,000 Btu/h |  |  | 9.0 EER
SPVHP (heating mode) nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  |  | 3.0 COP
|  |  | >30,000 and ≤36,000 Btu/h |  |  | 3.0 COP
Electrically Operated Room Air Conditioners
With louvered sides
|  |  | <6,000 Btu/h | 9.7 SEER | 11.0 CEER | 9.7 SEER
|  |  | ≥6,000 and <8,000 Btu/h | 9.7 EER | 11.0 CEER | 9.7 EER
|  |  | ≥8,000 and <14,000 Btu/h | 9.8 EER | 10.9 CEER | 9.8 EER
|  |  | ≥14,000 and <20,000 Btu/h | 9.7 EER | 10.7 CEER | 9.7 EER
|  |  | ≥20,000 and ≤25,000 Btu/h | 8.5 EER | 9.4 CEER | 8.5 EER
|  |  | >25,000 Btu/h | 8.5 EER | 9.0 CEER | 8.5 EER
Without louvered sides
|  |  | <6,000 Btu/h | 9.0 EER | 10.0 CEER | 9.0 EER
|  |  | ≥6,000 and <8,000 Btu/h | 9.0 EER | 10.0 CEER | 9.0 EER
|  |  | ≥8,000 and <11,000 Btu/h | 8.5 EER | 9.6 CEER | 8.5 EER
|  |  | ≥11,000 and <14,000 Btu/h | 8.5 EER | 9.5 CEER | 8.5 EER
|  |  | ≥14,000 and <20,000 Btu/h | 8.5 EER | 9.3 CEER | 8.5 EER
|  |  | ≥20,000 Btu/h | 8.5 EER | 9.4 CEER | 8.5 EER
Heat pumps with louvered sides
|  |  | <20,000 Btu/h | 9.0 EER | 9.8 CEER | 9.0 EER
|  |  | ≥20,000 Btu/h | 8.5 EER | 9.3 CEER | 8.5 EER
Heat pumps without louvered sides
|  |  | <14,000 Btu/h | 8.5 EER | 9.3 CEER | 8.5 EER
|  |  | ≥14,000 Btu/h | 8.0 EER | 8.7 CEER | 8.0 EER
|  | Casement only |  | 8.7 EER | 9.5 CEER | 8.7 EER
|  | Casement-slider |  | 9.5 EER | 10.4 CEER | 9.5 EER
Water Chiller, Air Cooled, with Condenser, Electrically Operated
|  |  | <150 tons: Path A | ≥10.100 EER FL ≥13.700 EER IPLV | ≥10.100 EER FL ≥13.700 EER IPLV | ≥10.100 EER FL ≥13.700 EER IPLV
|  |  | <150 tons: Path B | ≥9.700 EER FL ≥15.800 EER IPLV | ≥9.700 EER FL ≥15.800 EER IPLV | ≥9.700 EER FL ≥15.800 EER IPLV
|  |  | ≥150 tons: Path A | ≥10.100 EER FL ≥14.000 EER IPLV | ≥10.100 EER FL ≥14.000 EER IPLV | ≥10.100 EER FL ≥14.000 EER IPLV
|  |  | ≥150 tons: Path B | ≥9.7 EER FL ≥16.100 EER IPLV | ≥9.7 EER FL ≥16.100 EER IPLV | ≥9.7 EER FL ≥16.100 EER IPLV
Water Chiller, Air Cooled, without Condenser, Electrically Operated
|  |  | All Capacities | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements
Water Chiller, Water Cooled, Electrically Operated, Positive Displacement
|  |  | <75 tons: Path A | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV
|  |  | <75 tons: Path B | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥75 & <150 tons: Path A | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV
|  |  | ≥75 & <150 tons: Path B | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path A | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path B | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV
|  |  | ≥300 & <600 tons: Path A | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV
|  |  | ≥300 & <600 tons: Path B | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV
|  |  | ≥600 tons Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥600 tons Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
Water Chiller, Water Cooled, Electrically Operated, Centrifugal
|  |  | <150 tons: Path A | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV
|  |  | <150 tons: Path B | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path A | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV
|  |  | ≥150 & <300 tons: Path B | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV
|  |  | ≥300 & <400 tons: Path A | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV
|  |  | ≥300 & <400 tons: Path B | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV
|  |  | ≥400 & <600 tons: Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥400 & <600 tons: Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
|  |  | ≥600 tons: Path A | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV
|  |  | ≥600 tons: Path B | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV
Water Chiller, Air Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.600 COP FL | ≥0.600 COP FL | ≥0.600 COP FL
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Water Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.700 COP FL | ≥0.700 COP FL | ≥0.700 COP FL
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Absorption Double Effect, Indirect-Fired
|  |  | All Capacities: Path A | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Absorption Double Effect, Direct-Fired
|  |  | All Capacities: Path A | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.000 IPLV
|  |  | All Capacities: Path B | NA | NA | NA
Warm Air Furnaces and Combination Warm Air Furnaces/Air Conditioning Units
|  |  | Gas-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 80% AFUE or 80% Et | 78% AFUE or 80% Et
|  |  | Gas-Fired ≥225,000 Btu/h | 80% Et | 80% Et | 80% Et
|  |  | Oil-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 83% AFUE or 80% Et | 78% AFUE or 80% Et
|  |  | Oil-Fired ≥225,000 Btu/h | 81% Et | 81% Et | 81% Et
Warm Air Duct Furnaces
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec
Warm Air Unit Heaters
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec
|  |  | Oil-Fired | 80% Ec | 80% Ec | 80% Ec
Boilers, Gas-Fired
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 82% AFUE | 82% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 80% Et | 80% Et | 80% Et
|  | >2,500,000 Btu/h, Hot Water |  | 82% Ec | 82% Ec | 82% Ec
|  | <300,000 Btu/h, Steam |  | 75% AFUE | 84% AFUE | 80% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et
|  | >2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et
|  | ≥300,000 & ≤2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 79% Et
|  | >2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 79% Et
Boilers, Oil-Fired
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 84% AFUE | 84% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 82% Et | 82% Et | 82% Et
|  | >2,500,000 Btu/h, Hot Water |  | 84% Ec | 84% Ec | 84% Ec
|  | <300,000 Btu/h, Steam |  | 80% AFUE | 82% AFUE | 82% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et
|  | >2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et
Heat Rejection Equipment
|  | Propeller or axial fan open-circuit cooling towers |  | ≥40.2 gpm/hp | ≥40.2 gpm/hp | ≥40.2 gpm/hp
|  | Centrifugal fan open-circuit cooling towers |  | ≥20.0 gpm/hp | ≥20.0 gpm/hp | ≥20.0 gpm/hp
|  | Propeller or axial fan closed-circuit cooling towers |  | ≥14.0 gpm/hp | ≥16.1gpm/hp | ≥16.1gpm/hp
|  | Centrifugal fan closed-circuit cooling towers |  | ≥7.0 gpm/hp | ≥7.0 gpm/hp | ≥7.0 gpm/hp
|  | Propeller or axial fan evaporative condensers (Ammonia test fluid) |  | ≥134,000 Btu/h-hp | ≥134,000 Btu/h-hp | ≥134000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (Ammonia test fluid) |  | ≥110,000 Btu/h-hp | ≥110,000 Btu/h-hp | ≥110,000 Btu/h-hp
|  | Propeller or axial fan evaporative condensers (R-507A test fluid) |  | ≥157,000 Btu/h-hp | ≥157,000 Btu/h-hp | ≥157,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (R-507A test fluid) |  | ≥135,000 Btu/h-hp | ≥135,000 Btu/h-hp | ≥135,000 Btu/h-hp
|  | Air-cooled condensers |  | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp
Heat Transfer Equipment
|  | Liquid-to-Liquid, plate type heat exchangers |  | NR | NR | NR
Air Conditioners and Condensing Units Serving Computer Rooms
|  |  |  | Downflow/Upflow Units Minimum SCOP-127 Efficiency | Downflow/Upflow Units Minimum SCOP-127 Efficiency | Minimum Net SCOP
Air cooled
|  |  | <65,000 Btu/h | 2.20 / 2.09 | 2.20 / 2.09
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥240,000 Btu/h | 1.90 / 1.79 | 1.90 / 1.79
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.09
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.45
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.99
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.35
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.85
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.79
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.15
Water cooled
|  |  | <65,000 Btu/h | 2.60 / 2.49 | 2.60 / 2.49
|  |  | ≥65,000 & <240,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | ≥240,000 Btu/h | 2.40 / 2.29 | 2.40 / 2.29
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.5
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.25
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.7
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.6
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.25
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.05
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.45
Water cooled with fluid economizer
|  |  | <65,000 Btu/h | 2.55 / 2.44 | 2.55 / 2.44
|  |  | ≥65,000 & <240,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | ≥240,000 Btu/h | 2.35 / 2.24 | 2.35 / 2.24
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.45
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.6
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.1
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.55
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.05
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.4
Glycol cooled
|  |  | <65,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | ≥65,000 & <240,000 Btu/h | 2.15 / 2.04 | 2.15 / 2.04
|  |  | ≥240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.15
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.95
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.75
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
Glycol cooled with fluid economizer
|  |  | <65,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥240,000 Btu/h | 2.05 / 1.94 | 2.05 / 1.94
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.95
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.75
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.9
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.7
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
Variable Refrigerant Flow (VRF) Systems
VFR Multi-Split Air Conditioners, Air Cooled
|  |  | <65,000 Btu/h, All heating section |  |  | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.2 EER 15.5 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.0 EER 14.9 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.0 EER 13.9 IEER
VFR Multi-Split Heat Pumps, Air Cooled (Cooling Mode)
|  |  | <65,000 Btu/h, All heating section |  |  | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 11.0 EER 14.6 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.6 EER 13.9 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 9.5 EER 12.7 IEER
VFR Multi-Split with Heat Recovery Heat Pumps, Air Cooled (Cooling Mode)
|  |  | ≥65,000 & <135,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.8 EER 14.4 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric resistance (or none) heating section |  |  | 10.4 EER 13.7 IEER
|  |  | ≥240,000 Btu/h, Electric resistance (or none) heating section |  |  | 9.3 EER 12.5 IEER
VFR Multi-Split Heat Pumps, Water Source (Cooling Mode) 86º Entering Water
|  |  | <65,000 Btu/h, All heating section |  |  | 12.0 EER 16.0 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All heating section |  |  | 12.0 EER 16.0 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section |  |  | 10.0 EER 14.0 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 10.0 EER 12.0 IEER
VFR Multi-Split Heat Pumps with Heat Recovery, Water Source (Cooling Mode) 86º Entering Water
|  |  | <65,000 Btu/h, All heating section |  |  | 11.8 EER 15.8 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All heating section |  |  | 11.8 EER 15.8 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section |  |  | 9.8 EER 13.8 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 9.8 EER 11.8 IEER
VFR Multi-Split Heat Pumps, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 16.2 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 13.8 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 16.0 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 13.6 EER
VFR Multi-Split Heat Pumps, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 13.4 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 11.0 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All heating section |  |  | 13.2 EER
|  |  | ≥135,000 Btu/h, All heating section |  |  | 10.8 EER
VFR Multi-Split Heat Pumps, Air Cooled (Heating Mode)
|  |  | <65,000 Btu/h (cooling capacity) |  |  | 7.7 HSPF
≥65,000 & <135,000 Btu/h (cooling capacity)
|  |  | 47ºF db / 43ºF wb |  |  | 3.3 COP
|  |  | 17ºF db / 15ºF wb |  |  | 2.25 COP
≥135,000 (cooling capacity)
|  |  | 47ºF db / 43ºF wb |  |  | 3.2 COP
|  |  | 17ºF db / 15ºF wb |  |  | 2.05 COP
VFR Multi-Split Heat Pumps, Water Source (Heating Mode) 68º Entering Water
|  |  | <65,000 Btu/h (Cooling Capacity) |  |  | 4.3 COP
|  |  | ≥65,000 & <135,000 Btu/h (Cooling Capacity) |  |  | 4.3 COP
|  |  | ≥135,000 & <240,000 Btu/h (Cooling Capacity) |  |  | 4.0 COP
|  |  | ≥240,000 Btu/h (Cooling Capacity) |  |  | 3.9 COP
VFR Multi-Split Heat Pumps, Groundwater Source (Heating Mode) 50º Entering Water
|  |  | <135,000 Btu/h (cooling capacity) |  |  | 3.6 COP
|  |  | ≥135,000 Btu/h (cooling capacity) |  |  | 3.3 COP
VFR Multi-Split Heat Pumps, Ground Source (Heating Mode) 32º Entering Water
|  |  | <135,000 Btu/h (cooling capacity) |  |  | 3.1 COP
|  |  | ≥135,000 Btu/h (cooling capacity) |  |  | 2.8 COP
Vapor Compression Based Indoor Pool Dehumidifiers
|  | Single package indoor without air-cooled condenser (with or without economizer) |  |  |  | 3.5 MRE
|  | Single package water-cooled (with or without economizer) |  |  |  | 3.5 MRE
|  | Single package air-cooled (with or without economizer) |  |  |  | 3.5 MRE
|  | Split system air-cooled (with or without economizer) |  |  |  | 3.5 MRE
Dedicated Outdoor Air Units
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, without Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 4.9 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.0 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 2.7 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 4.8 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.0 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 2.0 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 3.2 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 3.5 ISCOP
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, with Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 5.3 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.6 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 3.3 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.8 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.8 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 3.8 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 4.0 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 4.8 ISCOP
HVAC Controls
Zone Thermostatic Controls
|  |  | Location | Within each zone | Within each zone | Within each zone
|  |  | Dwelling unit |  |  | Single zone
|  |  | Humidity control systems | At least one control per system where required | At least one control per system where required | Prevent simultaneous operation of humidification & dehumidification equipment
Prevent use of fossil fuel or electricity to produce >30% relative humidity in warmest zone or <60% relative humidity in coldest zone
|  |  | Perimeter system | Per each exterior exposure per orientation | Per each exterior exposure per orientation | Per each exterior exposure per orientation
|  |  | Dead band between heating & cooling | ≥5º | ≥5º | ≥5º
|  |  | Heating system supply water temperature reset based on outdoor temperature | Required | Required | Required on systems with ≥3 control valves
|  |  | Set point overlap restriction where separate heating & cooling controls located in zone | Required | Required | Required
Off-Hour Controls
|  |  | Automatic setback and shutdown | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor
|  |  | Setback capabilities | Down to 55° or Up to 85° | Down to 55° or Up to 85° | Adjustable heating ≥10° below occupied heating setpoint
Adjustable cooling ≥5° above occupied cooling setpoint or to prevent high space humidity levels
|  |  | Optimum start controls | Automatic start to achieve desired temperature just prior to scheduled occupancy | Automatic start to achieve desired temperature just prior to scheduled occupancy | On individual heating and cooling systems with setback controls and DDC
|  |  | Zone isolation | Required for nonsimultaneously occupied zones | Required for nonsimultaneously occupied zones | Required for nonsimultaneously occupied zones
|  |  |  | Isolation zones <25,000 sf or 1 floor | Isolation zones <25,000 sf or 1 floor | Isolation zones <25,000 sf or 1 floor
|  |  |  | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area
|  |  | Exceptions to off-hour controls | Zone that operate continuously | Zone that operate continuously | Continuous Operation
|  |  |  | Zone full HVAC load <6,800 Btu/h with readily accessible manual on/off | Zone full HVAC load <6,800 Btu/h with readily accessible manual on/off | Systems <15,000 Btu/h with readily accessible manual on/off
|  |  | Automatic HVAC Controls in Hotel/Motel Guest Rooms |  | In hotels & motels with >50 guest rooms | In hotels & motels with >50 guest rooms
[5 empty] | Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room | Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room
[5 empty] | Automatically lower occupant set point ≥4° in heating mode within 30 minutes of occupants leaving guest room | Automatically lower occupant set point ≥4° in heating mode within 30 minutes of occupants leaving guest room
[5 empty] | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode | When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode
[5 empty] | Within 30 of occupants leaving room, automatically turn off ventilation and exhaust fans or | Within 30 of occupants leaving room, automatically turn off ventilation and exhaust fans or
[5 empty] | Automatically shut off supply of outdoor air & shut off exhaust air | Automatically shut off supply of outdoor air & shut off exhaust air
[5 empty] | Captive key card systems permitted to be used to comply | Captive key card systems permitted to be used to comply
|  |  | Ventilation fans |  |  | Automatic off-hour shutoff required for fans >3/4 hp
Shutoff Dampers
|  |  | Stair and shaft vents, buildings ≥3 Stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Stair and shaft vents, buildings <3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Outdoor air supply (intake) & exhaust, buildings ≥3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Outdoor air supply, buildings <3 stories | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Exhaust/relief, buildings <3 stories | Gravity dampers with maximum leakage rate | Gravity dampers with maximum leakage rate | Gravity dampers w/ 20 cfm/sf maximum leakage rate
|  |  |  | 20 cfm/sf for dampers ≥24" in either dimension or | 20 cfm/sf for dampers ≥24" in either dimension or
|  |  |  | 40 cfm/sf for dampers <24" in either direction | 40 cfm/sf for dampers <24" in either direction
|  |  | Automatic shutoff damper controls | Required for motorized dampers | Required for motorized dampers | Required for motorized dampers
Heat Pump Auxiliary Heat Control
|  |  | Prevent internal electric resistance heater operation when heating load can be met by heat pump alone | Required | Required | Required
Protection Insulation
|  |  | Protection from sunlight, moisture, equipment maintenance, wind & solar radiation | Required | Required | Required
|  |  | Adhesive tape | Not permitted | Not permitted | Not permitted
Freeze Protection and Snow/Ice Melting Systems
|  |  | Automatic shutoff for freeze protection | >40º outside air temperature or when conditions of protected fluid will prevent freezing | >40º outside air temperature or when conditions of protected fluid will prevent freezing | >40º outside air temperature or when conditions of protected fluid will prevent freezing
|  |  | Automatic shutoff for melting systems | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature
Ventilation
|  |  |  | Capability to reduce to minimum required | Capability to reduce to minimum required
|  |  | Demand control ventilation to automatically reduce outside air intake during partial occupancy | Required for spaces >500 sf & average occupancy 25 persons per 1,000 sf & served by defined HVAC system | Required for spaces >500 sf & average occupancy ≥25 persons per 1,000 sf & served by defined HVAC system | Required for spaces >500 sf & design occupancy ≥25 persons per 1,000 sf & served by defined HVAC system
|  |  | Enclosed parking garages | ≥22,500 cfm total exhaust capacity or >1,125 cfm/hp: not utilizing heating or mechanical cooling | ≥22,500 cfm total exhaust capacity or >1,125 cfm/hp: not utilizing heating or mechanical cooling | ≥30,000 sq. ft. or <1,500 sq. ft/ hp: not utilizing heating or mechanical cooling
|  |  |  | Automatic air flow rate control to ≤50% based on contaminant levels or intermittently operate fans <20% of occupied time | Automatic air flow rate control to ≤50% based on contaminant levels or intermittently operate fans <20% of occupied time | Automatic air flow rate control to ≤50% based on contaminant levels
|  |  | Ventilation air heating control |  | For units serving multiple zones & operate in conjunction with zone heating & cooling systems
Not use heating or heat recovery to warm supply air >60℉ when
building loads or outdoor air temperature indicate majority of zones require cooling
Heated or Cooled Vestibules
|  |  | Controls |  | Shut off heating when outdoor air temperature >45℉ | Shut off heating when outdoor air temperature >45℉
[5 empty] | Thermostat located in vestibule | Thermostat located in vestibule
[5 empty] | Heating setpoint limit ≤60℉ | Heating setpoint limit ≤60℉
[5 empty] | Cooling setpoint limit ≥85℉ | Cooling setpoint limit ≥85℉
Direct Digital Control (DDC) Required Applications
New Buildings
|  |  | Air-handling system and all zones served by system |  |  | Individual system serving >3 zones & with fan system bhp ≥10 hp
|  |  | Chilled-water plant and all coils and terminal units served by system |  |  | Individual plants supplying >3 zones with design cooling capacity ≥300,000 Btu/h
|  |  | Hot-water plant and all coils and terminal units served by system |  |  | Individual plants supplying >3 zones with design heating capacity ≥300,000 Btu/h
Alteration or Addition
|  |  | Zone terminal unit |  |  | Where existing zones served by same air handling, chilled-water, or hot-water system have DDC
|  |  | Air-handling system or fan coil |  |  | Where existing air-handling system(s) and fan coil(s) served by same chilled- or hot-water plant have DDC
|  |  | New air-handling system and all new zones served by the system |  |  | Individual systems with fan system bhp ≥10 hp and supplying >3 zones and >75% zones are new
|  |  | New or upgraded chilled-water plant |  |  | Where all chillers are new and plant design cooling capacity ≥300,000 Btu/h
|  |  | New or upgraded hot-water plant |  |  | Where all boilers are new and plan design heating capacity ≥300,000 Btu/h
Direct Digital Control (DDC) Requirements
|  |  | Control capabilities |  |  | Monitoring zone & system demand for fan pressure, pump pressure, heating and cooling
Transferring zone & system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers
Automatically detecting those zones and systems that may be excessively driving reset logic and generate alarm or other indication to system operator
Readily allowing operator removal of zone(s) from reset algorithm
|  |  | DDC Display |  |  | Where required for new buildings, capable of trending and graphically displaying input and output points
|  |  | Chilled-water plant monitoring |  |  | Water-cooled plants >1,500 tons peak capacity
Air-cooled plants >860 tons peak capacity
Measure electric energy use and efficiency
15 minute trending
Graphical display for hourly, daily, monthly & annual data
≥36 months data storage
HVAC Construction and Insulation
Insulation for Supply & Return Ducts for Heating & Cooling, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-12
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6
|  |  | Indirectly conditioned space |  |  | R-1.9
Insulation for Supply & Return Ducts for Heating Only, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-12
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6
|  |  | Indirectly conditioned space |  |  | R-1.9
Insulation for Supply & Return Duct for Cooling Only, Located In
|  |  | Exterior & within building envelope separated from exterior or unconditioned space | ≥R-12 | ≥R-12 | R-8
|  |  | Unconditioned space & buried ducts | ≥R-6 | ≥R-6 | R-6
|  |  | Indirectly conditioned space |  |  | R-1.9
Heating System (Steam, Steam Condensate and Hot Water) Pipe Insulation
>350ºF Fluid Temperature & 0.32 - 0.34 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 4.5" | 4.5" | 4.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 5.0" | 5.0" | 5.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 5.0" | 5.0" | 5.0"
|  |  | 4" to <8" Nominal pipe or tube size | 5.0" | 5.0" | 5.0"
|  |  | ≥8" Nominal pipe or tube size | 5.0" | 5.0" | 5.0"
251-350ºF Fluid Temperature & 0.29 - 0.32 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 3.0" | 3.0" | 3.0"
|  |  | 1" to <1.5" Nominal pipe or tube size | 4.0" | 4.0" | 4.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 4.5" | 4.5" | 4.5"
|  |  | 4" to <8" Nominal pipe or tube size | 4.5" | 4.5" | 4.5"
|  |  | ≥8" Nominal pipe or tube size | 4.5" | 4.5" | 4.5"
201-250ºF Fluid Temperature & 0.27 - 0.30 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 2.5" | 2.5" | 2.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 2.5" | 2.5" | 2.5"
|  |  | 1.5" to <4" Nominal pipe or tube size | 2.5" | 2.5" | 2.5"
|  |  | 4" to <8" Nominal pipe or tube size | 3.0" | 3.0" | 3.0"
|  |  | ≥8" Nominal pipe or tube size | 3.0" | 3.0" | 3.0"
141-200ºF Fluid Temperature & 0.25 - 0.29 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
|  |  | 1.5" to <4" Nominal pipe or tube size | 2.0" | 2.0" | 2.0"
|  |  | 4" to <8" Nominal pipe or tube size | 2.0" | 2.0" | 2.0"
|  |  | ≥8" Nominal pipe or tube size | 2.0" | 2.0" | 2.0"
105-140ºF Fluid Temperature & 0.21 - 0.28 Insulation Conductivity (0.22 - 0.28 in ASHRAE)
|  |  | <1" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
|  |  | 4" to <8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
|  |  | ≥8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
Cooling Systems (Chilled Water, Brine, and Refrigerant) Pipe Insulation
40-60ºF Fluid Temperature & 0.21 - 0.27 Insulation Conductivity
|  |  | <1" Nominal pipe or tube Size | 0.5" | 0.5" | 0.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 0.5" | 0.5" | 0.5"
|  |  | 1.5" to <4" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 4" to <8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | ≥8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
<40ºF Fluid Temperature & 0.20 - 0.26 Insulation Conductivity
|  |  | <1" Nominal pipe or tube size | 0.5" | 0.5" | 0.5"
|  |  | 1" to <1.5" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | 1.5" to <4" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | 4" to <8" Nominal pipe or tube size | 1.0" | 1.0" | 1.0"
|  |  | ≥8" Nominal pipe or tube size | 1.5" | 1.5" | 1.5"
Sensible Panel Insulation
|  |  | Heating panel | R-3.5 on all surfaces not facing space being heated | R-3.5 on all surfaces not facing space being heated | R-3.5
|  |  | Radiant floor heating |  |  | R-3.5
|  |  | Heating panels in thermal envelope separating it from exterior | ≥R-value of insulation required in opaque assembly | ≥R-value of insulation required in opaque assembly | Adjacent envelope insulation counts toward requirement
Duct (Ductwork and Plenum) Sealing
|  |  | Ductwork and all plenums with pressure class ratings |  |  | Seal Class A
|  |  | Low-pressure duct systems | Fasten & seal all longitudinal and transverse joints, seams, and connections | Fasten & seal all longitudinal and transverse joints, seams, and connections
|  |  | Medium-pressure duct systems | Insulate & seal all ducts and plenums | Insulate & seal all ducts and plenums
|  |  | High-pressure duct systems | Insulate & seal all ducts | Insulate & seal all ducts
Duct and Plenum Leakage Tests
|  |  | Outside ductwork |  |  | Required leakage test for all
|  |  | >3 in. w.c. operating static pressure | Required leakage tests ≥25% of total duct area & documentation showing compliance submitted by designer | Required leakage tests ≥25% of total duct area & documentation showing compliance submitted by designer | Required leak tests ≥25% of total duct area selected by owner or owner representative
|  |  |  | Air leakage rate ≤4.0 | Air leakage rate ≤4.0 | Duct leakage class 6
Economizers
|  |  |  | Required on each cooling system (either air or water) | Either air or fluid economizer provided on: | Required on each cooling system (either air or fluid)
|  |  |  | ≥54,000 Btu/h individual fan-cooling units in buildings with other than Group R occupancy | ≥54,000 Btu/h individual fan-cooling units in buildings with other than Group R occupancy | ≥54,000 Btu/h individual fan-cooling units that serve non residential spaces
|  |  |  | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤300,000 Btu/h. | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤300,000 Btu/h. | 49% unit efficiency improvement is a compliance alternative to the economizer requirement
|  |  |  | ≥1,320,000 Btu/h total system capacity less capacity of units with air economizer of local water-cooled chilled water system | ≥1,320,000 Btu/h total system capacity less capacity of units with air economizer of local water-cooled chilled water system | ≥1,400,000 Btu/h total system capacity
|  |  |  | ≥1,720,000 Btu/h total system capacity less capacity of units with air economizers of air cooled chilled water systems or district chilled water systems | ≥1,720,000 Btu/h total system capacity less capacity of units with air economizers of air cooled chilled water systems or district chilled water systems | ≥270,000 Btu/h individual fan-cooling units that serve residential spaces
|  |  |  | ≥270,000 Btu/h individual fan-cooling units in building with Group R occupancy | ≥270,000 Btu/h individual fan-cooling units in building with Group R occupancy
|  |  |  | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤1,500,000 Btu/h. | Where total supply capacity of all fan cooling units without economizer is greater than ≤20% of total supply capacity in building or ≤1,500,000 Btu/h.
|  |  | Exceptions | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint | 25% air supplied to spaces designed to be humidified above 35℉ dewpoint
|  |  |  | Expected to operate <20 hour per week | Expected to operate <20 hour per week | Expected to operate <20 hour per week
|  |  |  | Serving supermarket area with open refrigerated case work | Serving supermarket area with open refrigerated case work | Serving supermarket area with open refrigerated case work
|  |  |  | Systems with heat recovery | Systems with heat recovery | Systems with condenser heat recovery
|  |  |  | Chilled-water cooling systems without a fan or use induction with capacity <1,400,000 Btu/h |  | In hospitals & ambulatory surgery centers where 75% air supplied to spaces designed to be humidified above 35℉ dewpoint
|  |  | Exceptions for computer rooms |  |  | Systems primarily serving computer rooms
a) Total design cooling load of all computer rooms <3,000,000 Btu/h & building not served by central chiller plant
b) Room design cooling load <600,000 Btu/h and building served by centralized chiller plant
c) Cooling towers not allowed by water authority
d) <600,000 Btu/h computer-room cooling equipment added to existing building
≥75% dedicated computer room systems serve:
a) Spaces classified as essential facility
b) Tier IV space
c) Space classified as critical operations power systems
d) Spaces where core financial transactions are cleared & settled
|  | Air economizer capacity |  | Outside air up to 100% of design supply air quantity | Outside air up to 100% of design supply air quantity | Outside air up to 100% of design supply air quantity
|  | Air economizer control signal |  | Sequenced with mechanical cooling equipment | Sequenced with mechanical cooling equipment | Sequenced with mechanical cooling equipment
|  |  |  | Not controlled by only mixed-air temperature | Not controlled by only mixed-air temperature | Not controlled by only mixed-air temperature
|  |  |  | Not increase heating energy use during normal operation | Not increase heating energy use during normal operation | Not increase heating energy use during normal operation
|  |  |  | Not capable of creating a false load | Not capable of creating a false load | Not capable of creating a false load
|  |  |  | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F
|  |  | Stages of mechanical cooling for direct expansion (DX) units directly controlled by space temperature | ≥2 stages for units ≥75,000 Btu/h | ≥2 stages for units ≥75,000 Btu/h | ≥2 stages for units ≥65,000 Btu/h
Direct expansion (DX) cooling stage requirements for modulating airflow units
|  |  | ≥65,000 and <240,000 Btu/h | ≥3 stages and ≤35% of full load compressor displacement | ≥3 stages and ≤35% of full load compressor displacement | ≥3 stages and ≤35% of full load compressor displacement
|  |  | ≥240,000 Btu/h | ≥4 stages and ≤25% of full load compressor displacement | ≥4 stages and ≤25% of full load compressor displacement | ≥4 stages and ≤25% of full load compressor displacement
|  |  | Air economizer high limit shutoff | Reduce outside air to minimum when it no longer reduces cooling energy usage | Reduce outside air to minimum when it no longer reduces cooling energy usage | Reduce outside air to minimum when it no longer reduces cooling energy usage
|  |  | Air economizer dampers (return, exhaust/relief, outdoor air) | ≤4 cfm/sf air leakage rate | ≤4 cfm/sf air leakage rate | ≤4 cfm/sf air leakage rate
|  |  | Preheat coils |  |  | Prevent heat output during mechanical cooling including economizer operation
|  | Water economizer |  | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb | Provide up to 100% of cooling load when outside air 50ºF db/45ºF wb
|  |  |  | Define exceptions for computer rooms with other economizers |  | Define exceptions for computer rooms with other economizers
Required for systems (required to have economizer) with dehumidification where 100% of cooling load can be met with water-cooled fluid economizer when outside air 45ºF db/40ºF wb
|  |  | Water economizer pressure drop | <15 ft. or secondary loop | <15 ft. or secondary loop | <15 ft. or secondary loop
|  |  | Water economizer control | Integrated with mechanical equipment to provide partial cooling | Integrated with mechanical equipment to provide partial cooling | Integrated with mechanical equipment to provide partial cooling
Economizer Fault Detection and Diagnostics
|  |  | Air-cooled unitary direct-expansion units and variable refrigerant flow (VRF) units with economizer | Outside, supply and return air sensors | Outside, supply and return air sensors | Outside, supply and return air sensors
|  |  |  | System status indication | System status indication | System status indication
|  |  |  | Capable of manual operation for independent testing & verification | Capable of manual operation for independent testing & verification | Capable of manual operation for independent testing & verification
|  |  |  | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats | Fault reporting to day-to-day operating personnel or annunciated locally on zone thermostats
|  |  |  | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air. | Capable of detecting sensor faults, control faults, damper faults and excess outdoor air.
Simultaneous Heating and Cooling Limitation
|  | Zone thermostatic controls |  | Configure controls to prevent simultaneous operation & to maintain deadband where separate heating & cooling controls are provided | Configure controls to prevent simultaneous operation & to maintain deadband where separate heating & cooling controls are provided | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled
|  |  | VAV control requirement before reheating, recooling or mixing takes place | Choose one of: | Choose one of: | Exception:
|  |  |  | 1) 30% of maximum supply air to each zone | 1) 30% of maximum supply air to each zone without DDC | Zone air flow <larger of:
|  |  |  | 2) ≤300 cfm where maximum flow rate <10% of total system supply airflow rate | 2) 20% of maximum supply air to each zone with DDC where | a) 20% of maximum supply air to each zone with DDC; 30% for other systems
|  |  |  | 3) Minimum ventilation requirements | Airflow in first stage of heating is deadband flow rate | b) Minimum ventilation requirements
|  |  |  | 4) Any higher rate demonstrated to reduce overall system annual energy use | Airflow in second stage of heating <50% zone design peak supply rate | c) Any higher rate demonstrated to reduce overall system annual energy use
|  |  |  | 5) Airflow rate required to comply with applicable code or accreditation standards | 3) Minimum ventilation requirements | d) Airflow rate required to comply with applicable code or accreditation standards
[5 empty] | 4) Any higher rate demonstrated to reduce overall system annual energy use | Exception:
[5 empty] | 5) Airflow rate required to comply with applicable code or accreditation standards | Zones with DDC, comply with all of:
1) Airflow rate in dead band does not exceed larger of:
1a) 20% zone design peak supply rate
1b)Minimum ventilation requirements
1c) Any higher rate demonstrated to reduce overall system annual energy use
1d) Airflow rate required to comply with applicable code or accreditation standards
2) Reheated, recooled or mixed air flow rate <50% zone design peak supply rate
3) First stage of heating modulates zone supply air temperature to maximum setpoint while airflow is maintained at dead band flow rate
4) Second stage of heating modulates airflow rate to heating maximum flow rate
|  | Supply air temperature reheat limit |  |  |  | Where allowed and duct openings are >6' above floor, supply air temperature ≤20º space temperature setpoint, except during warm-up
Hydronic system controls
|  |  | Three-pipe systems | Prohibited | Prohibited | Prohibited
|  |  | Two-pipe changeover systems | ≥15º F outside air temperature changeover deadband | ≥15º F outside air temperature changeover deadband | ≥15º F outside air temperature changeover deadband
|  |  |  | 4 hour minimum operations in one mode | 4 hour minimum operations in one mode | 4 hour minimum operations in one mode
|  |  |  | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart | Reset controls that allow heating and cooling supply temperature @ changeover point to be ≤30ºF apart
|  |  | Hydronic (water loop) heat pump systems | ≥20ºF deadband between rejection and addition | ≥20ºF deadband between rejection and addition | ≥20ºF deadband between rejection and addition
|  |  |  | Where open- or closed-circuit tower is used, provide separate heat exchanger to isolate tower loop from heat pump loop and automatic valve on tower loop; control heat loss by shutting down tower pump and closing valve | If closed-circuit tower, use either: | If closed-circuit tower, use either:
[5 empty] | Automatic valve to bypass all but minimal flow around tower or | Automatic valve to bypass all but minimal flow around tower or
[5 empty] | low-leakage positive closure dampers | low-leakage positive closure dampers
[5 empty] | If open-circuit tower, Automatic valve to bypass all water flow around tower | If open-circuit tower, Automatic valve to bypass all water flow around tower
[5 empty] | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop
|  |  |  | Two-position valves on each heat pump on systems with total pump system power >10 hp | Two-position valves on each heat pump on systems with total pump system power >10 hp | Two-position valves on each hydronic heat pump or water-cooled air conditioner
|  |  | Hydronic heat pump & water -cooled unitary air conditioners |  | Speed control or device that results ≤30% design wattage at 50% design flow | Speed control or device that results ≤30% design wattage at 50% design flow when total pump system power >5 hp
Humidifier preheat
|  |  | Preheating jackets mounted in airstream |  |  | Automatic shutoff valve
|  |  | Dispersion tube hot surface in airstream |  |  | ≥R-0.5 insulation
Air System Design and Control
|  | Fan power limitation |  | Fan systems >5 hp | Fan systems >5 hp | Fan systems >5 hp
Option 1: Fan system motor nameplate hp
|  |  | Constant volume | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011
|  |  | Variable volume | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015
Option 2: Fan system bhp
|  |  | Constant volume | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A
|  |  | Variable volume | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A
|  |  | Single zone variable air volume | Comply with constant volume fan power limitation | Comply with constant volume fan power limitation | Comply with constant volume fan power limitation
|  |  | Air systems with required air treatment or filtering, or heat recovery, or direct evaporation | Device adjustment tables | Device adjustment tables | Device adjustment tables
Motor Nameplate Horsepower
|  |  | For each fan | Fan brake horsepower indicated on construction documents | Fan brake horsepower indicated on construction documents | Fan brake horsepower indicated on construction documents
|  |  |  | Selected motor not larger than first available motor size greater than | Selected motor not larger than first available motor size greater than | Selected motor not larger than first available motor size greater than
|  |  |  | 1) 1.5 x fan bhp for fans <6 bhp | 1) 1.5 x fan bhp for fans <6 bhp | 1) 1.5 x fan bhp for fans <6 bhp
|  |  |  | 2) 1.3 x fan bhp for fans ≥6 bhp | 2) 1.3 x fan bhp for fans ≥6 bhp | 2) 1.3 x fan bhp for fans ≥6 bhp
|  |  |  | 3)Systems complying with fan power limitation Option 1 | 3)Systems complying with fan power limitation Option 1 | 3)Systems complying with fan power limitation Option 1
Fan efficiency
|  |  | Fan efficiency grade (FEG) | ≥67 | ≥67 | ≥67
|  |  | Total efficiency of fan @ design point of operation | Within 15% points of maximum total efficiency of the fan | Within 15% points of maximum total efficiency of the fan | Within 15% points of maximum total efficiency of the fan
|  | Fractional hp fan motors |  | ≥1/12 hp and <1 hp | ≥1/12 hp and <1 hp | ≥1/12 hp and <1 hp
|  |  |  | Electronically commutated motors or | Electronically commutated motors or | Electronically commutated motors or
|  |  |  | ≥70% motor efficiency | ≥70% motor efficiency | ≥70% motor efficiency
|  |  |  | Have means to adjust speed for either balancing or remote control | Have means to adjust speed for either balancing or remote control | Have means to adjust speed for either balancing or remote control
Fan airflow control
|  |  | Fans with variable-speed drive or vane-axial fans with variable-pitch blades or controls/devices resulting in <30% demand at 50% volume when static pressure = 1/3 Design |  |  | Requirement for variable airflow
|  |  | Supply air systems serving multiple zones | VAV required | VAV required
|  |  | Cooling systems required to vary air flow as function of load | For DX cooling system | For DX cooling system | For DX cooling system
|  |  |  | ≥65,000 Btu/h mechanical cooling capacity | ≥65,000 Btu/h mechanical cooling capacity | ≥65,000 Btu/h mechanical cooling capacity
|  |  |  | For chilled water and evaporative cooling systems | For chilled water and evaporative cooling systems | For chilled water and evaporative cooling systems
|  |  |  | ≥¼ hp fan motor | ≥¼ hp fan motor | ≥¼ hp fan motor
|  |  | Fan control for units that control mechanical cooling based on space temperature | ≥2 stages | ≥2 stages | ≥2 stages
|  |  |  | Low or minimum speed ≤66% of full speed | Low or minimum speed ≤66% of full speed | Low or minimum speed ≤66% of full speed
|  |  |  | Power draw at low or minimum speed ≤40% power at full speed | Power draw at low or minimum speed ≤40% power at full speed | Power draw at low or minimum speed ≤40% power at full speed
|  |  |  | Low or minimum speed used during low cooling load and ventilation-only operation | Low or minimum speed used during low cooling load and ventilation-only operation | Low or minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units that control space temperature by modulating airflow | Minimum speed ≤50% full speed | Minimum speed ≤50% full speed | Minimum speed ≤50% full speed
|  |  |  | Power draw at minimum speed ≤30% power at full speed | Power draw at minimum speed ≤30% power at full speed | Power draw at minimum speed ≤30% power at full speed
|  |  |  | Minimum speed used during low cooling load and ventilation-only operation | Minimum speed used during low cooling load and ventilation-only operation | Minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units with airside economizer | ≥2 speeds during economizer operation | ≥2 speeds during economizer operation | ≥2 speeds during economizer operation
Variable air volume (VAV) fan control
|  |  | Static pressure reset | For systems with direct digital control of individual zone boxes | For systems with direct digital control of individual zone boxes | For systems with direct digital control of individual zone boxes
|  |  |  | Control Capable of: | Control Capable of: | Control Capable of:
|  |  |  | 1) Automatic detection of any zone that excessively drives reset logic | 1) Automatic detection of any zone that excessively drives reset logic | 1) Automatic detection of any zone that excessively drives reset logic
|  |  |  | 2) Generating alarm | 2) Generating alarm | 2) Generating alarm
|  |  |  | 3) Allow operator to remove zone(s) from reset algorithm | 3) Allow operator to remove zone(s) from reset algorithm | 3) Allow operator to remove zone(s) from reset algorithm
|  |  | Ventilation optimization control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control
|  |  | Parallel-flow fan-powered VAV terminal control |  | Turn off terminal fan except when required for space heating or for ventilation | Turn off terminal fan except when required for space heating or for ventilation
[5 empty] | Turn on terminal fan as first stage heating before heating coil activation | Turn on terminal fan as first stage heating before heating coil activation
[5 empty] | During warmup or setback temperature control either | During warmup or setback temperature control either
[5 empty] | Operate terminal fan & heating coil without primary air or | Operate terminal fan & heating coil without primary air or
[5 empty] | Reverse terminal damper logic and heat with primary air | Reverse terminal damper logic and heat with primary air
|  |  | Supply-air temperature reset | Required for multiple zone HVAC systems | Required for multiple zone HVAC systems | Required for Multiple Zone HVAC Systems
Hydronic System Design and Control
Part load hydronic system controls
|  |  | Chilled or heated water systems for comfort conditioning control | Systems ≥500,000 Btu/h | Systems ≥300,000 Btu/h | Systems ≥300,000 Btu/h
|  |  | Automatic supply water temperature reset | Required | Required | Required
|  |  | Variable fluid flow control | Automatically vary fluid flow ≥50% on systems with combined motor capacity ≥10 hp and with ≥3 control valves | Automatically vary fluid flow ≥50% on systems with combined motor capacity ≥2 hp and with ≥3 control valves | Automatically vary fluid flow ≥75% or to minimum required flow rate on distribution systems with ≥3 control valves
|  |  |  | ≥50% on chilled water systems and heat rejection loops serving water cooled unitary air conditioners with combined motor capacity ≥10 hp | ≥50% on heating-water systems, chilled water systems and heat rejection loops serving water cooled unitary air conditioners with combined motor capacity ≥2 hp
|  |  | Variable flow systems | Speed control or multi-staged pumps | Speed control on pumps ≥7.5 hp | Speed control on individual or parallel pumps ≥7.5 hp
|  |  | Equipment isolation | Automatically reduce flow through chiller/boiler when chiller/boiler is shut down | Automatically reduce flow through chiller/boiler when chiller/boiler is shut down | Automatically shut off flow through chiller/boiler when chiller/boiler is shut down
|  |  | Boiler Controls | Automatic controls to sequence operations on multi-packaged boiler system | Automatic controls to sequence operations on multi-packaged boiler system | Turndown achieved with multiple single boilers and/or modulating boilers
|  |  |  | Multistage or modulating burner on single boiler systems ≥500,000 Btu/h | Multistage or modulating burner on single boiler systems ≥500,000 Btu/h
|  |  |  | Minimum boiler system turndown ratios | Minimum boiler system turndown ratios | Minimum boiler system turndown ratios
|  |  |  | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h | 3 to 1 on ≥1,000,000 & ≤5,000,000 Btu/h
|  |  |  | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h | 4 to 1 on >5,000,000 & ≤10,000,000 Btu/h
|  |  |  | 5 to 1 on >10,000,000 Btu/h | 5 to 1 on >10,000,000 Btu/h | 5 to 1 on >10,000,000 Btu/h
|  | Chilled-water coil selection |  |  |  | ≥15℉ temperature differential
≥57℉ leaving water temperature @ design conditions
Chilled water and condenser water pipe sizing
|  |  | Nominal size (inches) |  |  | Maximum design flow
≤2,000 operating hours per year, variable flow/variable speed
|  |  | 2.5" |  |  | 180 gpm
|  |  | 3" |  |  | 270 gpm
|  |  | 4" |  |  | 530 gpm
|  |  | 5" |  |  | 620 gpm
|  |  | 6" |  |  | 1100 gpm
|  |  | 8" |  |  | 1800 gpm
|  |  | 10" |  |  | 2700 gpm
|  |  | 12" |  |  | 3800 gpm
|  |  | >12" |  |  | 13.0 fps
≤2,000 operating hours per year, other
|  |  | 2.5" |  |  | 120 gpm
|  |  | 3" |  |  | 180 gpm
|  |  | 4" |  |  | 350 gpm
|  |  | 5" |  |  | 410 gpm
|  |  | 6" |  |  | 740 gpm
|  |  | 8" |  |  | 1200 gpm
|  |  | 10" |  |  | 1800 gpm
|  |  | 12" |  |  | 2500 gpm
|  |  | >12" |  |  | 8.5 fps
>2,000 and ≤4,400 operating hours per year, variable flow/variable speed
|  |  | 2.5" |  |  | 130 gpm
|  |  | 3" |  |  | 210 gpm
|  |  | 4" |  |  | 400 gpm
|  |  | 5" |  |  | 470 gpm
|  |  | 6" |  |  | 860 gpm
|  |  | 8" |  |  | 1400 gpm
|  |  | 10" |  |  | 2000 gpm
|  |  | 12" |  |  | 2900 gpm
|  |  | >12" |  |  | 9.5 fps
>2,000 and ≤4,400 operating hours per year, other
|  |  | 2.5" |  |  | 85 gpm
|  |  | 3" |  |  | 140 gpm
|  |  | 4" |  |  | 260 gpm
|  |  | 5" |  |  | 310 gpm
|  |  | 6" |  |  | 570 gpm
|  |  | 8" |  |  | 900 gpm
|  |  | 10" |  |  | 1300 gpm
|  |  | 12" |  |  | 1900 gpm
|  |  | >12" |  |  | 6.5 fps
>4,400 operating hours per year, variable flow/variable speed
|  |  | 2.5" |  |  | 110 gpm
|  |  | 3" |  |  | 170 gpm
|  |  | 4" |  |  | 320 gpm
|  |  | 5" |  |  | 370 gpm
|  |  | 6" |  |  | 680 gpm
|  |  | 8" |  |  | 1100 gpm
|  |  | 10" |  |  | 1600 gpm
|  |  | 12" |  |  | 2300 gpm
|  |  | >12" |  |  | 7.5 fps
>4,400 operating hours per year, other
|  |  | 2.5" |  |  | 68 gpm
|  |  | 3" |  |  | 110 gpm
|  |  | 4" |  |  | 210 gpm
|  |  | 5" |  |  | 250 gpm
|  |  | 6" |  |  | 440 gpm
|  |  | 8" |  |  | 700 gpm
|  |  | 10" |  |  | 1000 gpm
|  |  | 12" |  |  | 1500 gpm
|  |  | >12" |  |  | 5.0 fps
Heat Rejection Equipment
|  |  | Fan speed control |  | Individual motor or | Individual motor or
|  |  |  | Each fan ≥7.5 hp | array of motors ≥5 hp | array of motors ≥5 hp
|  |  | Multiple-cell equipment with variable speed fans | Operate maximum number of fans that comply with manufacturer's requirements for all components | Operate maximum number of fans that comply with manufacturer's requirements for all components | Operate maximum number of fans that comply with manufacturer's requirements for all components
|  |  |  | Operate all fans at same speed | Operate all fans at same speed | Operate all fans at same speed
|  |  | Limitation on centrifugal fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers
|  |  | Tower fan turndown | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell
Energy Recovery
|  |  | Energy recovery ventilation system | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air
|  |  |  | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate)
|  |  |  | Provisions to bypass or control energy recovery system to permit air economizer operation | Provisions to bypass or control energy recovery system to permit air economizer operation | Provisions to bypass or control energy recovery system to permit air economizer operation
|  |  |  | On systems operating <8,000 hours per year | On systems operating <8,000 hours per year | On systems operating <8,000 hours per year
|  |  | % outdoor air at full design airflow rate | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate
|  |  | ≥10% & <20% | ≥26,000 cfm | ≥26,000 cfm | ≥26,000 cfm
|  |  | ≥20% & <30% | ≥16,000 cfm | ≥16,000 cfm | ≥16,000 cfm
|  |  | ≥30% & <40% | ≥5,500 cfm | ≥5,500 cfm | ≥5,500 cfm
|  |  | ≥40% & <50% | ≥4,500 cfm | ≥4,500 cfm | ≥4,500 cfm
|  |  | ≥50% & <60% | ≥3,500 cfm | ≥3,500 cfm | ≥3,500 cfm
|  |  | ≥60% & <70% | ≥2,000 cfm | ≥2,000 cfm | ≥2,000 cfm
|  |  | ≥70% & <80% | ≥1,000 cfm | ≥1,000 cfm | ≥1,000 cfm
|  |  | ≥80% | ≥0 cfm | ≥0 cfm | ≥120 cfm
|  |  |  | Required on all systems operating ≥8,000 hours per year | Required on all systems operating ≥8,000 hours per year | Required on all systems operating ≥8,000 hours per year
|  |  | % outdoor air at full design airflow rate |  | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate
|  |  | ≥10% & <20% |  | ≥200 cfm | ≥200 cfm
|  |  | ≥20% & <30% |  | ≥130 cfm | ≥130 cfm
|  |  | ≥30% & <40% |  | ≥100 cfm | ≥100 cfm
|  |  | ≥40% & <50% |  | ≥80 cfm | ≥80 cfm
|  |  | ≥50% & <60% |  | ≥70 cfm | ≥70 cfm
|  |  | ≥60% & <70% |  | ≥60 cfm | ≥60 cfm
|  |  | ≥70% & <80% |  | ≥50 cfm | ≥50 cfm
|  |  | ≥80% |  | ≥40 cfm | ≥40 cfm
|  |  | Heat recovery for service water heating | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load
|  |  |  | Capacity to provide smaller of | Capacity to provide smaller of | Capacity to provide smaller of
|  |  |  | 1) 60% peak heat rejection load at design conditions | 1) 60% peak heat rejection load at design conditions | 1) 60% peak heat rejection load at design conditions
|  |  |  | 2) Preheating required to raise peak service hot water draw to 85°F | 2) Preheating required to raise peak service hot water draw to 85°F | 2) Preheating required to raise peak service hot water draw to 85°F
Exhaust Systems
|  |  | Kitchen exhaust systems | Replacement air directly into hood cavity ≤10% of hood airflow rate | Replacement air directly into hood cavity ≤10% of hood airflow rate | Replacement air directly into hood cavity ≤10% of hood airflow rate
|  |  |  | Conditioned supply air delivered to kitchen hood flow limitations | Conditioned supply air delivered to kitchen hood flow limitations | Conditioned supply air delivered to kitchen hood flow limitations
|  |  |  | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria
Performance testing required
|  |  | Fume (laboratory) hood systems that use exception for energy recovery | Variable exhaust & supply systems, or direct makeup supply for systems >defined cfm total exhaust | Variable exhaust & supply systems, or direct makeup supply for systems >defined cfm total exhaust | Variable exhaust & supply systems or heat recovery system for systems >5,000 cfm total exhaust
Radiant Heating Systems
|  |  | Unenclosed (outside building) spaces | Required and controlled by occupancy sensor or timer | Required and controlled by occupancy sensor or timer | Required and controlled when required
|  |  | Enclosed Spaces |  |  | Conform with governing standards
Hot Gas Bypass Limitation
Systems with Multiple Steps of Unloading (or Continuous Capacity Modulation in IECC)
|  |  | ≤240,000 Btu/h rated capacity | ≤50% maximum bypass capacity | ≤50% maximum bypass capacity | ≤15% maximum bypass capacity
|  |  | >240,000 Btu/h rated capacity | ≤25% maximum bypass capacity | ≤25% maximum bypass capacity | ≤10% maximum bypass capacity
Door Switches
|  |  | Any conditioned space with door, including doors with >50% glass, opening to outdoors |  |  | Doors provided with controls, that when door is open:
Disable mechanical heating or reset heating setpoint to ≤55° within 5 minutes of door opening
Disable mechanical cooling or reset cooling setpoint to ≥90° within 5 minutes of door opening.
Mechanical cooling may remain enabled if outdoor air temperature < space temperature
Exceptions:
Building entries with automatic closing devices
Space without thermostat
Alterations to existing buildings
Loading docks
Refrigeration Equipment Performance
|  |  |  | Energy use limits (kWh per day) | Energy use limits (kWh per day) | Energy use limits (kWh per day)
Commercial refrigeration, holding temperature application
|  |  | Refrigerator with solid doors | 0.10 x V + 2.04 | 0.10 x V + 2.04 | 0.10 x V + 2.04
|  |  | Refrigerator with transparent doors | 0.12 x V + 3.34 | 0.12 x V + 3.34 | 0.12 x V + 3.34
|  |  | Freezers with solid doors | 0.40 x V + 1.38 | 0.40 x V + 1.38 | 0.40 x V + 1.38
|  |  | Freezers with transparent doors | 0.75 x V + 4.10 | 0.75 x V + 4.10 | 0.75 x V + 4.10
|  |  | Refrigerators/freezers with solid doors | Greater of 0.12 x V + 3.34 or 0.70 | Greater of 0.12 x V + 3.34 or 0.70 | Greater of 0.12 x V + 3.34 or 0.70
Commercial refrigeration, pulldown application
|  |  | Commercial refrigerators | 0.126 x V +3.51 | 0.126 x V + 3.51 | 0.126 x V + 3.51
Commercial refrigerators and freezers, remote condensing
|  |  | Vertical open, medium temp | 0.82 x TDA + 4.07 | 0.82 x TDA + 4.07 | 0.82 x TDA + 4.07
|  |  | Semivertical open, medium temp | 0.83 x TDA + 3.18 | 0.83 x TDA + 3.18 | 0.83 x TDA + 3.18
|  |  | Horizontal open, medium temp | 0.35 x TDA + 2.88 | 0.35 x TDA + 2.88 | 0.35 x TDA + 2.88
|  |  | Vertical open, low temp | 0.27 x TDA + 6.85 | 2.27 x TDA + 6.85 | 0.27 x TDA + 6.85
|  |  | Horizontal open, low temp | 0.57 x TDA + 6.88 | 0.57 x TDA + 6.88 | 0.57 x TDA + 6.88
|  |  | Vertical transparent door, medium temp | 0.22 x TDA + 1.95 | 0.22 x TDA + 1.95 | 0.22 x TDA + 1.95
|  |  | Vertical transparent door, low temp | 0.56 x TDA + 2.61 | 0.56 x TDA + 2.61 | 0.56 x TDA + 2.61
|  |  | Service over counter, medium temp | 0.51 x TDA + 0.11 | 0.51 x TDA + 0.11 | 0.51 x TDA + 0.11
Commercial refrigerators and freezers, self-contained
|  |  | Vertical open, medium temp | 1.74 x TDA + 4.71 | 1.74 x TDA + 4.71 | 1.74 x TDA + 4.71
|  |  | Semivertical open, medium temp | 1.73 x TDA + 4.59 | 1.73 x TDA + 4.59 | 1.73 x TDA + 4.59
|  |  | Horizontal open, medium temp | 0.77 x TDA + 5.55 | 0.77 x TDA + 5.55 | 0.77 x TDA + 5.55
|  |  | Horizontal open, low temp | 1.92 x TDA + 7.08 | 1.92 x TDA + 7.08 | 1.92 x TDA + 7.08
|  |  | Vertical transparent door, ice cream temp | 0.67 x TDA + 3.29 | 0.67 x TDA + 3.29 | 0.67 x TDA + 3.29
|  |  | Vertical solid door, ice cream temp | 0.38 x V +0.88 | 0.38 x V +0.88 | 0.38 x V +0.88
|  |  | Horizontal transparent door, ice cream temp | 0.56 x TDA + 0.43 | 0.56 x TDA + 0.43 | 0.56 x TDA + 0.43
Commercial refrigerators and freezers, remote condensing
|  |  | Semivertical open, low temp | 2.27 x TDA + 6.85 | 2.27 x TDA + 6.85 | 2.27 x TDA + 6.85
|  |  | Vertical open, ice cream temp | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7
|  |  | Semivertical open, ice cream temp | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7
|  |  | Horizontal open, ice cream temp | 0.72 x TDA + 8.74 | 0.72 x TDA + 8.74 | 0.72 x TDA + 8.74
|  |  | Vertical transparent door, ice cream temp | 0.66 x TDA + 3.05 | 0.66 x TDA + 3.05 | 0.66 x TDA + 3.05
|  |  | Horizontal transparent door, medium temp | 0.16 x TDA + 0.13 | 0.16 x TDA + 0.13 | 0.16 x TDA + 0.13
|  |  | Horizontal transparent door, low temp | 0.34 x TDA + 0.26 | 0.34 x TDA + 0.26 | 0.34 x TDA + 0.26
|  |  | Horizontal transparent door, ice cream temp | 0.4 x TDA + 0.31 | 0.4 x TDA + 0.31 | 0.4 x TDA + 0.31
|  |  | Vertical solid door, medium temp | 0.11 x V + 0.26 | 0.11 x V + 0.26 | 0.11 x V + 0.26
|  |  | Vertical solid door, low temp | 0.23 x V + 0.54 | 0.23 x V + 0.54 | 0.23 x V + 0.54
|  |  | Vertical solid door, ice cream temp | 0.27 x V + 0.63 | 0.27 x V + 0.63 | 0.27 x V + 0.63
|  |  | Horizontal solid door, medium temp | 0.11 x V + 0.26 | 0.11 x V + 0.26 | 0.11 x V + 0.26
|  |  | Horizontal solid door, low temp | 0.23 x V + 0.54 | 0.23 x V + 0.54 | 0.23 x V + 0.54
|  |  | Horizontal solid door, ice cream temp | 0.27 x V + 0.63 | 0.27 x V + 0.63 | 0.27 x V + 0.63
|  |  | Service over counter, low temp | 1.08 x TDA + 0.22 | 1.08 x TDA + 0.22 | 1.08 x TDA + 0.22
|  |  | Service over counter, ice cream temp | 1.26 x TDA + 0.26 | 1.26 x TDA + 0.26 | 1.26 x TDA + 0.26
Commercial refrigerators and freezers, self-contained
|  |  | Vertical open, low temp | 4.37 x TDA + 11.82 | 4.37 x TDA + 11.82 | 4.37 x TDA + 11.82
|  |  | Vertical open, ice cream temp | 5.55 x TDA + 15.02 | 5.55 x TDA + 15.02 | 5.55 x TDA + 15.02
|  |  | Semivertical open, low temp | 4.34 x TDA + 11.51 | 4.34 x TDA + 11.51 | 4.34 x TDA + 11.51
|  |  | Semivertical open, ice cream temp | 5.52 x TDA + 14.63 | 5.52 x TDA + 14.63 | 5.52 x TDA + 14.63
|  |  | Horizontal open, ice cream temp | 2.44 x TDA + 9.0 | 2.44 x TDA + 9.0 | 2.44 x TDA + 9.0
|  |  | Service over counter, ice cream temp | 1.76 x TDA + 0.36 | 1.76 x TDA + 0.36 | 1.76 x TDA + 0.36
|  |  | Horizontal solid door, ice cream temp | 0.38 x V + 0.88 | 0.38 x V + 0.88 | 0.38 x V + 0.88
Walk-in Coolers & Walk-in Freezers that are NOT Either Site Assembled or Site Constructed
|  |  | Door-closers | Automatic within 1" of full closure | Automatic within 1" of full closure
|  |  | Doorway infiltration control | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method
|  |  | Walk-in coolers & refrigerated warehouse coolers: wall, ceiling and door insulation | ≥R-25 | ≥R-25
|  |  | Walk-in freezers & refrigerated warehouse freezers: wall, ceiling and door insulation | ≥R-32 | ≥R-32
|  |  | Walk-in freezer floor insulation | ≥R-28 | ≥R-28
|  |  | Transparent reach-in doors for walk-in freezers & windows in walk-in freezer doors | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass
|  |  | Windows & transparent reach-in doors for walk-in cooler doors | Double-pane or triple-pane, inert gas-filled, heat-reflective treated glass | Double-pane or triple-pane, inert gas-filled, heat-reflective treated glass
|  |  | Evaporative fan motors <1 hp and <460 v | Electronically commutated motors, brushless direct-current motors or 3-phase motors | Electronically commutated motors, brushless direct-current motors or 3-phase motors
|  |  | Condenser fan motors <1 hp | Electronically commutated motors, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors, permanent split capacitor-type motors or 3- phase motors
|  |  | Antisweat heaters without antisweat heater controls (total door rail, glass and frame heater power draw) | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers
|  |  |  | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers
|  |  | Antisweat heater control | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane
|  |  | Lights in walk-in coolers, walk-in freezers, and refrigerated warehouse freezers | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or
|  |  |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy
Walk-in Coolers and Walk-in Freezers that are Site Assembled or Site Constructed
|  |  | Door-closers | Automatic within 1" of full closure | Automatic within 1" of full closure | Automatic within 1" of full closure
|  |  | Doorway infiltration control | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method
|  |  | Insulation | ≥R-25 for walls | ≥R-25 for walls | ≥R-25 for walls
|  |  |  | ≥R-25 for ceiling | ≥R-25 for ceiling | ≥R-25 for ceiling
|  |  |  | ≥R-25 for cooler doors | ≥R-25 for cooler doors | ≥R-25 for cooler doors
|  |  |  | ≥R-32 for freezer doors | ≥R-32 for freezer doors | ≥R-32 for freezer doors
|  |  |  | ≥R-28 for freezer floor | ≥R-28 for freezer floor | ≥R-28 for freezer floor
|  |  | Transparent reach-in doors for walk-in freezers & windows in opaque walk-in freezer doors | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass
|  |  | Transparent reach-in doors for walk-in coolers & windows in opaque doors for walk-in coolers | Double-pane, inert gas-filled, heat-reflective treated glass | Double-pane, inert gas-filled, heat-reflective treated glass | Double-pane, inert gas-filled, heat-reflective treated glass, or triple-pane glass with inert gas or heat-reflective treated glass
|  |  | Evaporative fan motors <1 hp and <460 v | Electronically commutated motors or 3-phase motors | Electronically commutated motors or 3-phase motors | Electronically commutated motors (brushless direct-current motors) or 3-phase motors
|  |  | Condenser fan motors <1 hp | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors
|  |  | Antisweat heaters without antisweat heater controls (total door rail, glass and frame heater power draw) | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers
|  |  |  | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers
|  |  | Antisweat heater control | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane
|  |  | Lights | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or
|  |  |  | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy
|  |  | Walk-in freezer temperature based defrost termination control |  |  | First on upper temperature limit breach, second upon time limit breach
Performance Standards, (Effective January 1, 2020)
|  | Walk-in cooler & freezer display door efficiency |  |  | Maximum energy consumption (kWh/day)
|  |  | Display door, medium temperature |  | 0.04 × Add + 0.41
|  |  | Display door, low temperature |  | 0.15 × Add + 0.29
|  | Walk-in cooler & freezer nondisplay door efficiency |  |  | Maximum energy consumption (kWh/day)
|  |  | Passage door, medium temperature |  | 0.05 × Add + 0.17
|  |  | Passage door, low temperature |  | 0.14 × Add + 4.8
|  |  | Freight door, medium temperature |  | 0.04 × Add + 1.9
|  |  | Freight door low temperature |  | 0.12 × Add + 5.6
|  | Walk-in cooler & freezer refrigeration system efficiency |  |  | Minimum annual walk-in energy factor AWEF (Btu/w-h)
|  |  | Dedicated condensing, medium temperature, indoor system |  | 5.61
|  |  | Dedicated condensing, medium temperature, indoor system >9,000 Btu/h capacity |  | 5.61
|  |  | Dedicated condensing, medium temperature, outdoor system |  | 7.6
|  |  | Dedicated condensing, medium temperature, outdoor system >9,000 Btu/h capacity |  | 7.6
| Refrigerated Display Cases, Site Assembled or Site Constructed |  |  |  |  | All Cases
|  |  | Lighting & glass door control | Time switch to turn lights off during nonbusiness hours or | Time switch to turn lights off during nonbusiness hours or | Time switch to turn lights off during nonbusiness hours or
|  |  |  | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated
|  |  | Low-temperature display cases | Temperature-based defrost termination control with time-limit default | Temperature-based defrost termination control with time-limit default | Temperature-based defrost termination control with time-limit default
|  |  | Antisweat heater controls | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane
Refrigeration Systems
Refrigerated display cases, walk-in coolers or walk-in freezers served by remote compressors and remote condensers not located in a condensing unit (exception for working fluid that goes through both subcritical and super critical states or that uses ammonia refrigerant)
|  |  | Fan-powered condensers | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems
|  |  |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems
|  |  |  | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors
|  |  |  | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control
|  |  |  | Multiple fan condensers controlled in unison | Multiple fan condensers controlled in unison | Multiple fan condensers controlled in unison
|  |  |  | Minimum condensing temperature setpoint ≤70°F | Minimum condensing temperature setpoint ≤70°F | Minimum condensing temperature setpoint ≤70°F
|  |  | Compressor systems | Floating suction pressure control on compressors & multiple-compressor system suction groups | Floating suction pressure control on compressors & multiple-compressor system suction groups | Floating suction pressure control on compressors & multiple-compressor system suction groups
|  |  |  | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity
|  |  |  | Crankcase heaters cycled off during compressor operation | Crankcase heaters cycled off during compressor operation | Crankcase heaters cycled off during compressor operation
Alternate Compliance Path
|  | Computer room systems |  |  |  | HVAC systems serving heating, cooling or ventilating needs of computer room may comply with:
Computer room PUE1 ≤1.36
Highest value computer room PUE0 ≤1.36 where PEU0 calculated at 100% design IT equipment energy use and 50% design IT equipment energy
Provide documentation
Service Water Heating
|  | Water-heating equipment intended to be used to provide space heating |  | Allowed | Allowed | Allowed with conditions
|  |  |  | Meet minimum performance requirements for water-heating equipment | Meet minimum performance requirements for water-heating equipment | Allowed to provide space heating when one of following is met:
≤(13.3 × pmd 400)/𝑛, Btu/h standby loss
ahj agrees that single heat source will consume less energy than separate units
<150,000 Btu/h energy input of combined boiler & water heater system
Equipment Efficiency
High input-rated service water-heating-systems
|  |  |  | Gas-fired water heater in new building | Gas-fired water heater in new building | Gas-fired water heater in new building
|  |  | Singular piece serving entire building, rated ≥1,000,000 Btu/h | ≥90% Et | ≥90% Et | ≥90% Et
|  |  | Multiple pieces serving building, combined rated input ≥1,000,000 Btu/h | ≥90% Et, combined input-capacity-weighted-average | ≥90% Et, combined input-capacity-weighted-average | ≥90% Et, combined input-capacity-weighted-average
Electric table top water heaters
|  |  | ≤12 kW, Resistance, ≥20 gal (& ≤120 gal) |  | 0.93 - 0.00132V, EF | per 10 CFR Part 430
Electric water heaters
|  |  | ≤12 kW, Resistance, ≥20 gal (& ≤55 gal) | 0.97 - 0.00132V, EF | 0.960 - 0.0003V, EF | per 10 CFR Part 430
|  |  | ≤12 kW grid-enabled >75 gal & ≤120 gal |  | 1.061 - 0.00168V, EF
|  |  | >12 kW, Resistance, (≥20 gal) | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h
|  |  | ≤24 amps and ≤250 volt, heat pump, (>55 gal & ≤120 gal) | 0.93 - 0.00132V, EF | 2.057 - 0.00113V, EF | per 10 CFR Part 430
Gas storage water heaters
|  |  | ≤75,000 Btu/h, ≥20 gal (& ≤55 gal) | 0.67 - 0.0019V, EF | 0.675 - 0.0015V, EF | per 10 CFR Part 430
|  |  | ≤75,000 Btu/h, >55 gal & ≤100 gal |  | 0.8012 - 0.00078V, EF
|  |  | >75,000 Btu/h, < 4,000 (Btu/h)/gal |  |  | 80% Et (Q/800 + 110√V) SL, Btu/h
|  |  | >75,000 and ≤155,000 Btu/h, < 4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
|  |  | >155,000 Btu/h, <4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Gas instantaneous water heaters
|  |  | >50,000 and <200,000 Btu/h, ≥4,000 (Btu/h)/gal and <2 gal | 0.62 - 0.0019V, EF | 0.82 - 0.0019V, EF | per 10 CFR Part 430
|  |  | ≥200,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
|  |  | ≥200,000 Btu/h, ≥4,000 (Btu/h)/gal and ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Oil storage water heaters
|  |  | ≤105,000 Btu/h, ≥20 gal (& ≤50 gal) | 0.59 - 0.0019V, EF | 0.68 - 0.0019V, EF | per 10 CFR Part 430
|  |  | >105,000 Btu/h, <4,000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Oil instantaneous water heaters
|  |  | ≤210,000 Btu/h, ≥4,000 (Btu/h)/gal and <2 gal | 0.59 - 0.0019V, EF | 0.59 - 0.0019V, EF | per 10 CFR Part 430
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal and ≥10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h
Hot water supply boilers, gas and oil
|  |  | ≥300,000 and <12,500,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
Hot water supply boilers, gas
|  |  | ≥300,000 and <12,500,000 Btu/h ≥4,000 (Btu/h)/gal and ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Hot water supply boilers, oil
|  |  | >300,000 and <12,500,000 Btu/h ≥4,000 (Btu/h)/gal and >10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h
|  | Pool Heaters, Oil and Gas |  | 82% Et | 82% Et | per 10 CFR Part 430
|  | Heat Pump Pool Heaters |  | 4.0 COP | 4.0 COP | 4.0 COP
|  | Unfired Storage Tanks |  | ≥R-12.5 | ≥R-12.5 | R-12.5
Heat Traps
|  |  | Vertical risers serving storage water heaters and storage tanks serving noncirculating systems | Supplied internal heat traps or provided with heat traps on supply and discharge piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping
Service Hot Water Piping Insulation
|  |  | Insulate | Inlet & outlet piping to heat trap or first 8 feet | Inlet & outlet piping to heat trap or first 8 feet | Recirculating system piping
|  |  |  | Piping that is heat traced | Piping that is heat traced | First 8' of outlet piping for constant temperature nonrecirculating storage system
First 8' of branch piping connecting to recirculating, heat trace-traced or impedance piping
Inlet piping between storage tank and heat trap in nonrecirculating storage system
Externally heated piping (heat trace or impedance heating)
|  |  | Minimum pipe insulation thickness | Use mechanical section requirements (Table C403.2.10) | Use mechanical section requirements (Table C403.11.3) | Use mechanical section requirements (Table 6.8.3-1)
Efficient Heated Water Supply Piping
|  |  | Heated water supply piping | Maximum flow rate | Maximum flow rate
|  |  |  | 1/4", ≤0.5 gpm | 1/4", ≤0.5 gpm
|  |  |  | 5/16", ≤1 gpm | 5/16", ≤1 gpm
|  |  |  | 3/8", ≤1.5 gpm | 3/8", ≤1.5 gpm
Maximum allowable pipe length method
|  | Nominal pipe size to public lavatory faucets |  | Maximum piping length | Maximum piping length
|  |  | 1/4" | 6' | 6'
|  |  | 5/16" | 4' | 4'
|  |  | 3/8" | 3' | 3'
|  |  | 1/2" | 2' | 2'
|  |  | 5/8" | 1' | 1'
|  |  | 3/4" | 0.5' | 0.5'
|  |  | 7/8" | 0.5' | 0.5'
|  |  | 1" | 0.5' | 0.5'
|  |  | 1¼" | 0.5' | 0.5'
|  |  | 1½" | 0.5' | 0.5'
|  |  | ≥2" | 0.5' | 0.5'
|  | Nominal pipe size to other fixtures and appliances |  | Maximum piping length | Maximum piping length
|  |  | 1/4" | 50' | 50'
|  |  | 5/16" | 50' | 50'
|  |  | 3/8" | 50' | 50'
|  |  | 1/2" | 43' | 43'
|  |  | 5/8" | 32' | 32'
|  |  | 3/4" | 21' | 21'
|  |  | 7/8" | 16' | 16'
|  |  | 1" | 13' | 13'
|  |  | 1¼" | 8' | 8'
|  |  | 1½" | 6' | 6'
|  |  | ≥2" | 4' | 4'
Maximum allowable pipe volume method
|  |  | For public lavatory faucets | <2 ounces | <2 ounces
|  |  | For other plumbing fixtures or plumbing appliances | <0.5 gallons | <0.5 gallons
|  |  | Water volume determination | Internal volumes of pipe, fittings, valves, meters and manifolds between nearest source and termination of fixture supply piping using volumes below | Internal volumes of pipe, fittings, valves, meters and manifolds between nearest source and termination of fixture supply piping using volumes below
|  | Nominal pipe size |  | Volume (liquid ounces per foot length) | Volume (liquid ounces per foot length)
|  |  | 1/4" | 0.33 | 0.33
|  |  | 5/16" | 0.5 | 0.5
|  |  | 3/8" | 0.75 | 0.75
|  |  | 1/2" | 1.5 | 1.5
|  |  | 5/8" | 2 | 2
|  |  | 3/4" | 3 | 3
|  |  | 7/8" | 4 | 4
|  |  | 1" | 5 | 5
|  |  | 1¼" | 8 | 8
|  |  | 1½" | 11 | 11
|  |  | ≥2" | 18 | 18
Heated-water circulating and temperature maintenance systems
|  |  | Circulation systems | Provided with a circulation pump and return pipe or cold water supply pipe | Provide circulation pump and return pipe or cold water supply pipe
|  |  |  | Automatically turns on pump when demand for hot water | Automatically turns on pump when demand for hot water
|  |  |  | Automatically turns off pump when at desired temperature & no hot water demand | Automatically turns off pump when at desired temperature & no hot water demand
|  |  | Electric heat trace systems | Automatically adjusts energy input to maintain desired water temperature in pipe during time heated water is used in the occupancy | Automatically adjusts energy input to maintain desired water temperature in pipe during time heated water is used in the occupancy
|  |  |  | Automatically turns off when no hot water demand | Automatically turns off when no hot water demand
|  |  | Controls for hot water storage | Pumping water between water heater and heated-water storage limited to <5 minutes after end of cycle | Pumping water between water heater and heated-water storage limited to <5 minutes after end of cycle
| Demand Recirculation Controls |  |  | Demand recirculation water system pumps from heated-water supply pipe back to heated-water source through cold-water supply pipe | Demand recirculation water system pumps from heated-water supply pipe back to heated-water source through cold-water supply pipe
|  |  | Required controls | Start pumping upon receiving signal from | Start pumping upon receiving signal from
|  |  |  | Action of a user | Action of a user
|  |  |  | Sensing the presence of a user | Sensing the presence of a user
|  |  |  | Sensing flow of water | Sensing flow of water
|  |  |  | Limit temperature of water entering cold-water piping to 104°F | Limit temperature of water entering cold-water piping to 104°F
Service Water Heating System Controls
|  |  | Storage temperature controls |  |  | Setpoint ≤120ºF or temperature compatible with intended use
|  |  | Temperature maintenance controls in hot water pipes |  |  | Automatic time switches/controls for extended periods when hot water not required
|  |  | Outlet temperature controls for lavatory faucets in public restrooms |  |  | Delivered ≤110ºF
|  |  | Circulating pump controls for storage tanks | Limit operation to 5 minutes after heating cycle | Limit operation to 5 minutes after heating cycle | Limit operation to 5 minutes after heating cycle
Drain Water Heat Recovery Units
|  |  |  | Comply with CSA B55.2 | Comply with CSA B55.2
|  |  |  | Potable water-side pressure loss <10 psi at maximum design flow | Potable water-side pressure loss <10 psi at maximum design flow
|  |  |  | For Group R occupancies drain water heat recovery unit efficiency in accordance with CSA B55.1 | For Group R occupancies drain water heat recovery unit efficiency in accordance with CSA B55.1
Energy Consumption of Pools and In Ground Permanent Spas
Pool heaters
|  |  | Electric power to all heaters | Readily accessible on-off switch without adjusting setpoint | Readily accessible on-off switch without adjusting setpoint | Readily accessible on-off switch without adjusting setpoint
|  |  | Natural as-fired heaters | No continuously burning pilot | No continuously burning pilot | No continuously burning pilot
|  |  | Time switches | Installed on heaters and pumps | Installed on heaters and pumps | Installed on swimming pool heaters and pumps
Pool covers
|  |  |  | On outdoor heated pools & outdoor spas | On outdoor heated pools & outdoor spas | On heated pools
|  |  | Water temperature ≤90ºF | Vapor retardant cover required | Vapor retardant cover required | Vapor retardant cover required
|  |  | Water temperature >90ºF | Vapor retardant cover required | Vapor retardant cover required | Vapor retardant cover required with ≥R-12 insulation
Portable spas
|  |  | Control requirements | Meet APSP 14 | Meet APSP 14
Power
|  |  | Combined Feeder & Branch Circuit Voltage Drop |  | ≤5% Total | ≤5% Total
|  |  | Individual dwelling units | Separately metered in use group R-2 | Separately metered in use group R-2
|  |  | Automatic receptacle control |  |  | ≥50% of all 125v 15-& 20-ampere receptacles in:
Private offices
Conference rooms
Rooms used primarily for printing and/or copying functions
Break rooms
Classrooms
Individual workstations
≥25% branch circuit feeders installed for modular furniture not shown on construction documents
Functions on:
Scheduled basis or
Occupant sensor or
Signal from another control system
Electrical energy monitoring
|  |  | Applicability |  |  | New buildings
Exceptions:
Buildings <25,000 sf
Individual tenant spaces <10,000 sf
Dwelling units
Residential buildings with <10,000 sf of common area
Critical and equipment branches of NEC Article 517
|  |  | Separately monitored area |  |  | Total building
Each individual tenant space, excluding shared systems
|  |  | Separately monitored energy use |  |  | Total electrical energy
HVAC systems
Interior lighting
Exterior lighting
Receptacle circuits
|  |  | Recording and reporting |  |  | Recorded minimum of every 15 minutes
Reported at least hourly, daily, monthly and annually
Store data for ≥36 months
Low Voltage Dry-Type Distribution Transformers
|  |  | Single phase (kVA) | Minimum efficiency | Minimum efficiency | Efficiency
|  |  | 15 | 97.7% | 97.7% | 97.7%
|  |  | 25 | 98% | 98% | 98%
|  |  | 37.5 | 98.2% | 98.2% | 98.2%
|  |  | 50 | 98.3% | 98.3% | 98.3%
|  |  | 75 | 98.5% | 98.5% | 98.5%
|  |  | 100 | 98.6% | 98.6% | 98.6%
|  |  | 167 | 98.7% | 98.7% | 98.7%
|  |  | 250 | 98.8% | 98.8% | 98.8%
|  |  | 333 | 98.9% | 98.9% | 98.9%
|  |  | Three phase (kVA) | Minimum efficiency | Minimum efficiency | Efficiency
|  |  | 15 | 97% | 97.89% | 97.89%
|  |  | 30 | 97.5% | 98.23% | 98.23%
|  |  | 45 | 97.7% | 98.4% | 98.4%
|  |  | 75 | 98% | 98.6% | 98.6%
|  |  | 112.5 | 98.2% | 98.74% | 98.74%
|  |  | 150 | 98.3% | 98.83% | 98.83%
|  |  | 225 | 98.5% | 98.94% | 98.94%
|  |  | 300 | 98.6% | 99.02% | 99.02%
|  |  | 500 | 98.7% | 99.14% | 99.14%
|  |  | 750 | 98.8% | 99.23% | 99.23%
|  |  | 1000 | 98.9% | 99.28% | 99.28%
Completion Requirements
|  |  | Record Drawings of Actual Installation |  |  | Construction documents to require submittal within 30 days of system acceptance
|  |  | Operating Manual |  |  | Construction documents to require submittal
|  |  | Maintenance Manual |  |  | Construction documents to require submittal
Lighting
Alterations
|  |  | Alterations requiring compliance with lighting power density | Replacement ≥50% of luminaires in a space or increased installed lighting power | Replacement ≥10% of luminaires or increases installed lighting power | Interior alterations involving >20% connected lighting load of space or area
|  |  |  | Replacement ≥10% of luminaires or increases installed lighting power |  | Interior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
Exterior alterations involving >20% connected lighting load of space or area
Exterior alterations involving ≤20% connected lighting load of space or area need NOT comply but can not increase installed lighting power
Exterior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
|  |  | Alterations requiring compliance with control requirements | Replacement ≥50% of luminaires in a space | Replacement ≥10% of luminaires or increases installed lighting power | Interior alterations involving >20% connected lighting load except for daylight controls
Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
Automatic/scheduled shutoff controls for interior lamp plus ballasts/drivers or one-for-one luminaire replacement
Automatic shutoff & power reduction controls for exterior alterations involving >20% connected lighting load of space or area
Automatic/scheduled shutoff controls for exterior lamp plus ballasts/drivers or one-for-one luminaire replacement
| Luminaire Wattage |  |  |  |  | Lighting power calculations for ballasts with adjustable ballast factors shall be based on the ballast factor that will be used in the space provided that the ballast factor is not user changeable.
| Lighting In Dwelling Units in Commercial Buildings |  |  | Exception when ≥75% lamps in permanently installed fixture are High-efficacy lamps or when ≥75% permanently installed interior fixtures fitted with high-efficiency lamps | ≥90% permanently installed interior fixtures contain only high-efficiency lamps or comply with Sections C405.2.4 & C405.3 | Exception
Lighting Controls
Interior Lighting Control
|  |  | Control device for each interior enclosed space (area) | Required controls vary with space type | Required controls vary by space type | All lighting control functions indicated in Table 9.6.1
[5 empty] | Luminaire level lighting controls (LLLC) vary by space type & independently capable of: | Functions labeled "REQ" are mandatory
1) If space type labeled "ADD1", ≥1 of those functions implemented in space
[5 empty] | Brightening or dimming lighting based on occupant activity | 2) If space type labeled "ADD2", ≥1 of those functions implemented in space
[5 empty] | Brightening or dimming artificial lighting to maintain desired light level | Functions:
Local control: ≥1 manual lighting controls in the space
Restricted to manual ON
[5 empty] | Modifying performance parameters to account for control strategy changes, configurations & reconfigurations | Restricted to partial automatic ON
Bilevel lighting control
Automatic daylight responsive controls for sidelighting
Automatic daylight responsive controls for toplighting
Automatic partial OFF (full OFF complies)
Automatic full OFF
Scheduled shutoff
|  |  | Time-switch control (Automatic interior lighting shutoff controls for all spaces) | Each area not provided with occupant sensor controls | Each area not provided with occupant sensor controls | All lighting (except emergency lighting that is automatically off during normal operation) automatically off during scheduled unoccupied periods
|  |  |  | Provided with manual control | Provided with manual control
|  |  |  | Control functions | Control functions | Scheduled OFF
|  |  |  | ≥7-day clock | ≥7-day clock | Controlled by:
|  |  |  | 7 different day types per week | 7 different day types per week | Time-of-day device
|  |  |  | Incorporate automatic holiday feature | Incorporate automatic holiday feature | Signal from another automatic control or alarm/security system
|  |  |  | >10 hour program backup capability | >10 hour program backup capability
|  |  |  | ≤2 hour manual override | ≤2 hour manual override
|  |  |  | Individual override switch controls area ≤5,000 sq. ft. | Individual override switch controls area ≤5,000 sq. ft.
|  |  | Occupancy sensor space control | Occupancy sensor controls required in: | Occupant sensor controls required in: | In space types per Table 9.6.1
|  |  |  | Classrooms / lecture / training rooms | Classrooms / lecture / training rooms
|  |  |  | Conference / meeting/ multipurpose rooms | Conference / meeting / multipurpose rooms
|  |  |  | Copy / print rooms | Copy / print rooms
|  |  |  | Lounges | Lounges / breakrooms
|  |  |  | Employee lunch & break rooms | Enclosed offices
|  |  |  | Private offices | Open plan office areas
|  |  |  | Restrooms | Restrooms
|  |  |  | Storage rooms | Storage rooms
Janitorial closets
|  |  |  | Locker rooms | Locker rooms
|  |  |  | Other spaces ≤300 sq. ft. enclosed by floor-to-ceiling height partitions | Other spaces ≤300 sq. ft. enclosed by floor-to-ceiling height partitions
|  |  |  | Warehouses | Warehouse storage areas
|  |  | Occupant sensor control function | Occupancy sensors shall be: | Occupant sensors shall be: | Per Table 9.6.1
|  |  |  | Automatic off within 30 minutes; | Automatic off within 20 minutes; | Restricted to manual ON
|  |  |  | Manual on or automatic on to ≤50% power; | Manual on or automatic on to ≤50% power; | Restricted to partial ON: ≤50% automatically turn on and remainder to be manually turned on
|  |  |  | Manual off control to allow occupants to turn off lights | Manual off control to allow occupants to turn off lights
Automatic partial OFF (full OFF complies): automatically reduces lighting by ≥50% within 20 minutes of occupants leaving
Automatic full OFF within 20 minutes of occupants leaving
|  |  | Occupant sensor control function in warehouses | Automatically reduce lighting power ≥50% in isleways and open areas | Automatically reduce lighting power ≥50% in isleways and open areas
|  |  |  | Independently control lighting in each isleway | Independently control lighting in each isleway
|  |  |  | Not control lighting beyond isleway being controlled | Not control lighting beyond isleway being controlled
|  |  | Light-reduction controls | Manual control capable to reduce connected load ≤50% in reasonably uniform pattern | Manual control capable to reduce connected load ≤50% in reasonably uniform pattern | Bilevel lighting control: Step between full ON and full OFF to be between 30% & 70% of full lighting power
|  |  | Manual controls | Readily accessible and located where the controlled lights are | Readily accessible and located where the controlled lights are | Readily accessible and located where the controlled lights are
|  |  | Daylight responsive controls | Control lighting in spaces with >150 watts of general lighting within sidelight daylight zone | Control lighting in spaces with >150 watts of general lighting within sidelit zone | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within primary sidelight daylight zone
|  |  |  | Control lighting in spaces with >150 watts of general lighting within toplight daylight zone | Control lighting in spaces with >150 watts of general lighting within toplit zone | Photocontrol lighting in spaces with ≥300 watts of general lighting completely or partially within primary and secondary sidelight daylight zone
|  |  |  | Exceptions: | Exceptions: | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within daylight areas under skylights & roof monitors
|  |  |  | 1) Direct patient care space in health care facility | 1) Direct patient care space in health care facility
|  |  |  | 2) Dwelling & sleeping units | 2) Lighting require to have specific application control
|  |  |  | 3) Lighting require to have specific application control | 3) Sidelit zones on first floor above grade in Group A-2 and Group M occupancies
|  |  |  | 4) Sidelight daylight zones on first floor above grade in Group A-2 and Group M occupancies | 4) New buildings where total connected lighting powered ≤ adjusted interior lighting power allowance calculated per Equation 4-9
|  |  | Daylight-responsive control functions (Daylight zone control) | Lights in toplight daylight zones controlled independently of lights in sidelight daylight zones | Lights in toplit zones controlled independently of lights in sidelit zones | General lighting in secondary sidelighted area controlled independently of primary sidelight area
|  |  |  | Configured to be calibrated from within that space by authorized personnel | Configured to be calibrated from within that space by authorized personnel | General lighting in overlapping toplighted and sidelighted daylight areas controlled together
|  |  |  | Readily accessible calibration mechanism | Readily accessible calibration mechanism | Readily accessible calibration mechanism
|  |  |  | Continuous dimming controls from full light output to ≤15% of full light output in offices, classrooms, laboratories and library reading rooms | Continuous dimming controls from full light output to ≤15% of full light output in offices, classrooms, laboratories and library reading rooms | Photocontrol to reduce lighting by continuous dimming or with one control point between 50% & 70%, with second control point between 20% & 40% (or lowest dimming level the technology allows) and third control point is OFF
|  |  |  | Capable of complete shutoff of all controlled lights | Capable of complete shutoff of all controlled lights
|  |  |  | Independent control of lights in sidelight daylight zones facing different cardinal orientations | Independent control of lights in sidelit zones facing different cardinal orientations
|  |  | Sidelight daylight zone | Floor area next to vertical fenestration | Floor area adjacent to vertical fenestration | Primary sidelight area
|  |  |  | Where fenestration located in a wall, | Where fenestration located in a wall, | Directly adjacent to vertical fenestration
|  |  |  | Extends laterally to nearest full-height wall, or up to 1.0 times height from floor to top of fenestration | Extends laterally to nearest full-height wall, or up to 1.0 times height from floor to top of fenestration | Width is width of fenestration plus, on each side, the smaller of:
1) ½ fenestration head height (floor to top of glazing) or
|  |  |  | Extends longitudinally from edge of fenestration to nearest full-height wall, or 2 feet, whichever is less | Extends longitudinally from edge of fenestration to nearest full-height wall, or 2 feet, whichever is less | 2) Distance to opaque vertical obstruction ≥5' high
Depth is smaller of perpendicular distance from fenestration:
1) Vertical head height or
|  |  |  | Area of fenestration ≥ 24 sq. ft. | Area of fenestration ≥ 24 sq. ft. | 2) Distance to opaque vertical obstruction ≥5' high
|  |  |  | Distance from fenestration to any building or geological formation which would block access to daylight is greater than height from bottom of fenestration to top of building or geological formation | Distance from fenestration to any building or geological formation which would block access to daylight is greater than height from bottom of fenestration to top of building or geological formation | Secondary sidelight area
Directly adjacent to primary sidelight area
Width is width of fenestration plus, on each side, the smaller of:
1) ½ fenestration head height (floor to top of glazing) or
2) Distance to opaque vertical obstruction ≥5' high
Depth is smaller of perpendicular distance from fenestration:
|  |  |  | Where located in existing building, visible transmittance of fenestration ≥0.2 | Where located in existing building, visible transmittance of fenestration ≥0.2 | 1) Vertical head height or
2) Distance to opaque vertical obstruction ≥5' high
Secondary sidelight area
If primary sidelight area ends at opaque vertical obstruction ≥5' high, there is no secondary sidelight area
|  |  |  | Where fenestration located in a rooftop monitor, |  | Daylight area under roof monitor
|  |  |  | Extends laterally to nearest obstruction that is taller than 0.7 times ceiling height, or up to 1.0 times height from floor to bottom of fenestration, whichever is less |  | Width is width of fenestration plus, on each side, the smaller of:
1) 2 ft or
2) Distance to opaque vertical obstruction ≥5' high or
|  |  |  | Extends longitudinally from edge of fenestration to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.25 times height from floor to bottom of fenestration, whichever is less |  | 3) Distance to edge of any primary sidelighted area
Depth is smaller inward distance from bottom edge of fenestration:
1) Monitor sill height (floor to bottom edge of glazing) or
2) Distance to nearest opaque vertical obstruction, where any part of obstruction is farther than the difference between height of obstruction and monitor sill height
|  |  | Toplight daylight zone | Floor area underneath roof fenestration assembly | Floor area underneath roof fenestration assembly | Daylight area under skylight
|  |  |  | Extends laterally and longitudinally beyond edge of roof fenestration assembly to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.7 times ceiling height, whichever is less | Extends laterally and longitudinally beyond edge of roof fenestration assembly to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.7 times ceiling height, whichever is less | Area bounded by opening beneath skylight & horizontally in each direction, smaller of:
a) 70% ceiling height or
b) Distance to nearest opaque vertical obstruction where any part of obstruction is father than 70% distance between top of obstruction & ceiling at lowest edge of skylight
Where fenestration located in a rooftop monitor,
Extends laterally to nearest obstruction that is taller than 0.7 times ceiling height, or up to 1.0 times height from floor to bottom of fenestration, whichever is less
Extends longitudinally from edge of fenestration to nearest obstruction that is taller than 0.7 times ceiling height, or up to 0.25 times height from floor to bottom of fenestration, whichever is less
|  |  |  | No building or geological formation blocks direct sunlight from hitting assembly at peak solar angle on summer solstice | No building or geological formation blocks direct sunlight from hitting assembly at peak solar angle on summer solstice
|  |  |  | Where located in existing building, the product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylight zone ≥0.008 | Product of visible transmittance of assembly and area of rough opening of assembly divided by area of daylit zone ≥0.008
Specific application controls
Wattage only exempt if in addition to general lighting & is independently controlled
|  |  | Display/accent lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Separate control device
|  |  | Case lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Separate control device
|  |  | Hotel, motel sleeping units and guest suites | Master control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room | Control device or system capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room
Separate occupant sensing control for bathrooms
|  |  | Supplemental task lighting | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power) | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power)
|  |  | Permanently installed luminaires in dwelling units |  | Occupant sensor or light reduction controls
|  |  | Nonvisual lighting | Dedicated control independent of controls for other lighting within room or space | Time-switch control independent of controls for other lighting within room or space | Separate control device
|  |  | Demonstration lighting | Dedicated control independent of controls for other lighting within room or space | Controlled by occupant sensor or time-switch plus manual switch for separate control from general lighting | Separate control device
|  |  | Parking Garage Lighting Control |  |  | Automatic lighting shutoff
Automatic ≥30% reduction when no activity ≤20 minutes
≥50% automatic reduction from sunset to sunrise on covered vehicle entrance & exit ramps
Photocontrol dimming within 20' of wall with ≥40% window wall ratio & no exterior obstructions
|  | Exterior lighting controls |  | Automatic shut-off when sufficient daylight available | Automatic shut-off when sufficient daylight available | Automatic shut-off when sufficient daylight available
|  |  |  | Facade or landscape lighting automatically shuts as function of dusk/dawn and set opening and closing time | Facade & landscape lighting automatically shuts off set 1 hour after business closing to ≤1 hour before business opening | Facade and landscape lighting automatically off between midnight or business closing and 6 am or business opening
|  |  |  | Other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes | Other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to ≥6 am, from ≤1 hour after business closing to ≥1 hour before business opening or during any period when activity not detected for >15 minutes | Signage & other than facade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes
| Functional Testing |  |  | In commissioning section | In commissioning section | In each section
| Exit Signs |  |  | ≤5 watts per side for internally illuminated
Interior Lighting Power
|  | Building Area Method - Lighting Power Densities |  | Standard Section C405
|  |  |  | w/sf | w/sf | w/sf
|  |  | Automotive Facility | 0.8 | 0.71 | 0.71
|  |  | Convention Center | 1.01 | 0.76 | 0.76
|  |  | Courthouse | 1.01 | 0.9 | 0.9
|  |  | Dining: Bar Lounge/Leisure | 1.01 | 0.9 | 0.9
|  |  | Dining: Cafeteria/Fast Food | 0.9 | 0.79 | 0.79
|  |  | Dining: Family | 0.95 | 0.78 | 0.78
|  |  | Dormitory | 0.57 | 0.61 | 0.61
|  |  | Exercise Center | 0.84 | 0.65 | 0.65
|  |  | Fire Station | 0.67 | 0.53 | 0.53
|  |  | Gymnasium | 0.94 | 0.68 | 0.68
|  |  | Healthcare - Clinic | 0.9 | 0.82 | 0.82
|  |  | Hospital | 1.05 | 1.05 | 1.05
|  |  | Hotel | 0.87 | 0.75 | 0.75
|  |  | Library | 1.19 | 0.78 | 0.78
|  |  | Manufacturing Facility | 1.17 | 0.9 | 0.9
|  |  | Motel | 0.87 | 0.75 | 0.75
|  |  | Motion Picture Theater | 0.76 | 0.83 | 0.83
|  |  | Multi-Family | 0.51 | 0.68 | 0.68
|  |  | Museum | 1.02 | 1.06 | 1.06
|  |  | Office | 0.82 | 0.79 | 0.79
|  |  | Parking Garage | 0.21 | 0.15 | 0.15
|  |  | Penitentiary | 0.81 | 0.75 | 0.75
|  |  | Performing Arts Theater | 1.39 | 1.18 | 1.18
|  |  | Police Station | 0.87 | 0.8 | 0.8
|  |  | Post Office | 0.87 | 0.67 | 0.67
|  |  | Religious Building | 1 | 0.94 | 0.94
|  |  | Retail | 1.26 | 1.06 | 1.06
|  |  | School/University | 0.87 | 0.81 | 0.81
|  |  | Sports Arena | 0.91 | 0.87 | 0.87
|  |  | Town Hall | 0.89 | 0.8 | 0.8
|  |  | Transportation | 0.7 | 0.61 | 0.61
|  |  | Warehouse | 0.66 | 0.48 | 0.48
|  |  | Workshop | 1.19 | 0.9 | 0.9
Space-by-Space Method, Common Space Types - Lighting Power Densities
|  | (Space with Multiple Functions Shall Be Broken up Into Smaller Subspaces) |  | Standard Section C405 |  | w/sf | RCR Threshold
Atrium - First 40' in height
|  |  | Atrium <40' in height | 0.03 per ft (total height) | 0.03 per ft (total height)
|  |  | Atrium <20' in height |  |  | 0.03 | N/A
|  |  | Atrium ≥20' and ≤40' |  |  | 0.03 | N/A
|  |  | Atrium >40' in height | 0.40 + 0.02 per foot in total height | 0.40 + 0.02 per foot in total height | 0.40 + 0.02 per foot in total height | N/A
|  |  | Audience seating area in auditorium | 0.63 | 0.63 | 0.63 | 6
|  |  | Audience seating area in convention center | 0.82 | 0.82 | 0.82 | 4
|  |  | Audience seating area in gymnasium | 0.65 | 0.65 | 0.65 | 6
|  |  | Audience seating area in performing arts theatre | 2.43 | 2.03 | 2.03 | 8
|  |  | Audience seating area in motion picture theatre | 1.14 | 1.14 | 1.14 | 4
|  |  | Audience seating area in penitentiary | 0.28 | 0.28 | 0.28 | 4
|  |  | Audience seating area in religious building | 1.53 | 1.53 | 1.53 | 4
|  |  | Audience seating area in sports arena | 0.43 | 0.43 | 0.43 | 4
|  |  | Audience seating area in other | 0.43 | 0.43 | 0.43 | 4
|  |  | Banking activity area | 1.01 | 0.86 | 0.86 | 6
|  |  | Classroom / lecture hall / training room in penitentiary | 1.34 | 1.34 | 1.34 | 4
|  |  | Classroom / lecture hall / training room in other | 1.24 | 0.96 | 0.92 | 4
|  |  | Conference / meeting / multipurpose room | 1.23 | 1.07 | 1.07 | 6
|  |  | Confinement cells |  |  | 0.81 | 6
|  |  | Copy / print room | 0.72 | 0.56 | 0.56 | 6
|  | Corridor in facility for visually impaired (and not used primarily by staff) |  | 0.92 | 0.92 | 0.92 | Width <8'
|  |  | Corridor in hospital | 0.79 | 0.92 | 0.92 | Width <8'
|  |  | Corridor in manufacturing facility | 0.41 | 0.29 | 0.29 | Width <8'
|  |  | Corridor in other | 0.66 | 0.66 | 0.66 | Width <8'
|  |  | Courtroom | 1.72 | 1.39 | 1.39 | 6
|  |  | Computer room | 1.71 | 1.33 | 1.33 | 4
|  |  | Dining area in penitentiary | 0.96 | 0.96 | 0.96 | 6
|  | Dining area in facility for visually impaired (and not used primarily by staff) |  | 1.9 | 2 | 2 | 4
|  |  | Dining area in bar/lounge or leisure Dining | 1.07 | 0.93 | 0.93 | 4
|  |  | Dining area in cafeteria or fast food dining | 0.65 | 0.63 | 0.63 | 4
|  |  | Dining area in family dining | 0.89 | 0.71 | 0.71 | 4
|  |  | Dining area in other | 0.65 | 0.63 | 0.63 | 4
|  |  | Electrical / mechanical room | 0.95 | 0.43 | 0.43 | 6
|  |  | Emergency vehicle garage | 0.56 | 0.41 | 0.41 | 4
|  |  | Food preparation area | 1.21 | 1.06 | 1.06 | 6
|  |  | Guest room | 0.47 | 0.77 | 0.77 | 6
|  |  | Laboratory in or as classroom | 1.43 | 1.2 | 1.2 | 6
|  |  | Laboratory, otherwise | 1.81 | 1.45 | 1.45 | 6
|  |  | Laundry / washing area | 0.6 | 0.43 | 0.43 | 4
|  |  | Loading dock, interior | 0.47 | 0.58 | 0.58 | 6
|  | Lobby in facility for visually impaired (and not used primarily by staff) |  | 1.8 | 2.03 | 2.03 | 4
|  |  | Lobby for elevator | 0.64 | 0.68 | 0.69 | 6
|  |  | Lobby in hotel | 1.06 | 1.06 | 1.06 | 4
|  |  | Lobby in performing arts theater | 2 | 1.7 | 1.7 | 6
|  |  | Lobby in motion picture theater | 0.59 | 0.45 | 0.45 | 4
|  |  | Lobby, otherwise | 0.9 | 1 | 1 | 4
|  |  | Locker Room | 0.75 | 0.48 | 0.48 | 6
|  |  | Lounge / breakroom in healthcare facility | 0.92 | 0.78 | 0.78 | 6
|  |  | Lounge / breakroom, otherwise | 0.73 | 0.62 | 0.62 | 4
|  |  | Office - enclosed | 1.11 | 0.93 | 0.93 (≤250 sf) | 8
[6 empty] | 0.93 (>250 sf) | 8
|  |  | Office - open plan | 0.98 | 0.81 | 0.81 | 4
|  |  | Parking area, interior | 0.19 | 0.14 | 0.14 | 4
|  |  | Pharmacy area | 1.68 | 1.34 | 1.34 | 6
|  | Restroom in facility for visually impaired (and not used primarily by staff) |  | 1.21 | 0.96 | 0.96 | 8
|  |  | Restroom, otherwise | 0.98 | 0.85 | 0.85 | 8
|  |  | Sales Area (for Accent Lighting see Additional Interior Lighting | 1.59 | 1.22 | 1.22 | 6
|  |  | Seating area, general | 0.54 | 0.42 | 0.42 | 4
|  |  | Stairway |  |  | Use space LPD containing stairway
|  |  | Stairwell | 0.69 | 0.58 | 0.58 | 10
|  |  | Storage room | 0.63 | 0.46 | 0.46 | 6
|  |  | Storage room <50 sf |  |  | 0.97 | 6
|  |  | Storage room ≥50 sf & ≤1,000 sf |  |  | 0.46 | 6
|  |  | Vehicular maintenance area | 0.67 | 0.56 | 0.56 | 4
|  |  | Workshop | 1.59 | 1.14 | 1.14 | 6
|  | Space-by-Space Method, Building-Specific Space Types - Lighting Power Densities |  | Standard Section C405 |  | w/sf | RCR Threshold
Facility for visually impaired
|  |  | Chapel (and not used primarily by staff) | 2.21 | 1.06 | 1.06 | 4
|  |  | Recreation room / common living room(and not used primarily by staff) | 2.41 | 1.8 | 1.8 | 6
|  |  | Convention center exhibit space | 1.45 | 0.88 | 0.88 | 4
|  |  | Dormitory - Living Quarters | 0.38 | 0.54 | 0.54 | 8
|  |  | Fire station sleeping quarters | 0.22 | 0.2 | 0.2 | 6
Gymnasium / fitness center
|  |  | Exercise area | 0.72 | 0.5 | 0.5 | 4
|  |  | Playing Area | 1.2 | 0.82 | 0.82 | 4
Healthcare facility
|  |  | Exam/Treatment | 1.66 | 1.68 | 1.68 | 8
|  |  | Medical Supply | 0.74 | 0.54 | 0.54 | 6
|  |  | Nursery | 0.88 | 1 | 1 | 6
|  |  | Nurses' Station | 0.71 | 0.81 | 0.81 | 6
|  |  | Operating Room | 2.48 | 2.17 | 2.17 | 6
|  |  | Patient Room | 0.62 | 0.62 | 0.62 | 6
|  |  | Physical Therapy | 0.91 | 0.84 | 0.84 | 6
|  |  | Radiology / Imaging | 1.51 | 1.06 | 1.06 | 6
|  |  | Recovery | 1.15 | 1.03 | 1.03 | 6
Library
|  |  | Reading area | 1.06 | 0.82 | 0.82 | 4
|  |  | Stacks | 1.71 | 1.2 | 1.2 | 4
Manufacturing
Corridor / transition
|  |  | Detailed manufacturing | 1.29 | 0.93 | 0.93 | 4
|  |  | Equipment room | 0.74 | 0.65 | 0.65 | 6
|  |  | Extra high bay (>50' ceiling height) | 1.05 | 1.05 | 1.05 | 4
|  |  | High bay (25' - 50' ceiling height) | 1.23 | 0.75 | 0.75 | 4
|  |  | Low bay (<25' ceiling height) | 1.19 | 0.96 | 0.96 | 4
Museum
|  |  | General exhibition | 1.05 | 1.05 | 1.05 | 6
|  |  | restoration | 1.02 | 0.85 | 0.85 | 6
|  |  | Performing art theater - dressing room | 0.61 | 0.36 | 0.36 | 6
|  |  | Post office - sorting area | 0.94 | 0.68 | 0.68 | 4
Religious buildings
|  |  | Fellowship hall | 0.64 | 0.55 | 0.55 | 4
|  |  | Worship pulpit, choir | 1.53 | 1.53 | 1.53 | 4
Retail
|  |  | Dressing / fitting room | 0.71 | 0.5 | 0.5 | 8
|  |  | Mall concourse | 1.1 | 0.9 | 0.9 | 4
Sales area (for accent lighting see additional interior lighting)
Sports arena - playing area
|  |  | Class 4 facility | 1.2 | 1.13 | 1.13 | 4
|  |  | Class 3 facility | 1.8 | 1.7 | 1.7 | 4
|  |  | Class 2 facility | 2.4 | 1.96 | 1.96 | 4
|  |  | Class 1 facility | 3.68 | 2.47 | 2.47 | 4
Transportation facility
|  |  | Baggage / carousel area | 0.53 | 0.45 | 0.45 | 4
|  |  | Airport - concourse | 0.36 | 0.31 | 0.31 | 4
|  |  | Terminal - ticket counter | 0.8 | 0.62 | 0.62 | 4
Warehouse storage area
|  |  | Medium to bulky, palletized items | 0.58 | 0.35 | 0.35 | 4
|  |  | Smaller, hand-carried items | 0.95 | 0.69 | 0.69 | 6
|  |  | Room Geometry Adjustment when using space-by-space method |  |  | Allowed for individual spaces where empty room RCR is >threshold, LPD increase = base space LPD x 0.20
|  |  | Additional interior lighting power when using space-by-space method for specific lighting functions | For specified luminaires and not used for any other purpose | For specified luminaires and not used for any other purpose | For specified lighting function and not for any other purpose
|  |  |  | Controlled separately from general lighting | Automatically controlled separately from general lighting | Automatically controlled separately from general lighting
|  |  |  | Turn off during nonbusiness hours | Turn off during nonbusiness hours | Turn off during nonbusiness hours
|  |  |  | ≤1.0 w/sf of such space for decorative appearance or for highlighting art or exhibits | ≤0.9 w/sf in lobbies & ≤0.75 w/sf in other spaces for decorative appearance or for highlighting art or exhibits | ≤0.75 w/sf for decorative appearance or for highlighting art or exhibits
|  |  |  | In sales area to highlight merchandise, Additional ILPA = 500 w + (Retail Area 1 x 0.6 w/sf) + (Retail Area 2 x 0.6 w/sf) + (Retail Area 3 x 1.4 w/sf) + (Retail Area 4 x 2.5 w/sf) | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.87 w/sf) | In sales area to highlight merchandise, Additional ILPA = 1000 w + (Retail Area 1 x 0.45 w/sf) + (Retail Area 2 x 0.45 w/sf) + (Retail Area 3 x 1.05 w/sf) + (Retail Area 4 x 1.88 w/sf)
|  | Additional Interior Lighting Power using non-mandatory controls |  |  |  | Allowed when using space-by-space method and when all mandatory controls are used
* Limited to workstation-specific luminaires
** Occupant allowed to select preferred light level
*** Cannot be used to satisfy exemption
Control Factors
Manual, continuous dimming controls or programmable multi-level dimming control
|  |  | Open office |  |  | 0.05
|  |  | Private office |  |  | 0.05
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  | 0.1
|  |  | Retail sales area |  |  | 0.1
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  | 0
Programmable multi-level dimming control using programmable time scheduling
|  |  | Open office |  |  | 0.05
|  |  | Private office |  |  | 0.05
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  | 0.1
|  |  | Retail sales area |  |  | 0.1
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  | 0.1
Occupancy sensors controlling downlight component of workstation specific luminaires with continuous dimming to OFF capabilities
|  |  | Open office |  |  | 0.25*
|  |  | Private office |  |  | 0
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  | 0
|  |  | Retail sales area |  |  | 0
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  | 0
Occupancy sensors controlling downlight component of workstation specific luminaires with continuous dimming to OFF capabilities in combination with personal continuous dimming control of downlight illumination by workstation occupant
|  |  | Open office |  |  | 0.30* **
|  |  | Private office |  |  | 0
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  | 0
|  |  | Retail sales area |  |  | 0
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  | 0
Automatic continuous daylight dimming in secondary sidelighted areas
|  |  | Open office |  |  | 0.10***
|  |  | Private office |  |  | 0.10***
|  |  | Conference room, meeting room, classroom (lecture/training) |  |  | 0.10***
|  |  | Retail sales area |  |  | 0.10***
|  |  | Lobby, atrium, dining area, corridors/stairways, gym/pool, mall concourse, parking garage |  |  | 0.10***
Exterior Lighting
Lighting Power Limits for Building Exteriors
Zone 0: undeveloped area within national parks, state parks, forest land, rural areas and other undeveloped areas defined by authority having jurisdiction
|  | Zone 0: Tradable surfaces |  |  |  | No allowance
Zone 0: Nontradable surfaces
|  |  | Roadway/parking entry, trail head, & toilet facility, or other locations approved by authority having jurisdiction |  |  | Single luminaire ≤25 w
Zone 1: developed areas of national parks, state parks, forest land and rural areas
Zone 1: Tradable surfaces
|  |  | Base site allowance | 500 w | 350 w | 350 w
|  |  | Uncovered parking areas and drives | 0.04 w/sf | 0.03 w/sf | 0.03 w/sf
|  |  | Walkways <10 ft wide | 0.7 w/lin ft | 0.5 w/lin ft | 0.5 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.14 w/sf | 0.10 w/sf | 0.10 w/sf
|  |  | Dining areas |  | 0.65 w/sf | 0.65 w/sf
|  |  | Stairways | 0.75 w/sf | 0.60 w/sf | 0.60 w/sf
|  |  | Pedestrian tunnels | 0.15 w/sf | 0.12 w/sf | 0.12 w/sf
|  |  | Landscaping |  | 0.03 w/sf | 0.03 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 20 w/lin ft of Door Width | 14 w/lin ft of opening | 14 w/lin ft of opening
|  |  | Entry canopies | 0.25 w/sf | 0.20 w/sf | 0.20 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.60 w/sf | 0.40 w/sf | 0.40 w/sf
|  |  | Outdoor open sales areas | 0.25 w/sf | 0.2 w/sf | 0.2 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | No Allowance | No Allowance | No Allowance
|  | Zone 1: Non-tradable surfaces |  |  | Additional exterior lighting power allowance
|  |  | Building facades | No Allowance | No Allowance | No Allowance
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry
Zone 2: areas predominantly consisting of residential zoning, neighborhood business districts, light industrial with limited night-time use & residential mixed use areas
Zone 2: Tradable surfaces
|  |  | Base site allowance | 600 w | 400 w | 400 w
|  |  | Uncovered parking areas and drives | 0.06 w/sf | 0.04 w/sf | 0.04 w/sf
|  |  | Walkways <10 ft wide | 0.7 w/lin ft | 0.5 w/lin ft | 0.5 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.14 w/sf | 0.10 w/sf | 0.10 w/sf
|  |  | Dining areas |  | 0.65 w/sf | 0.65 w/sf
|  |  | Stairways | 1.0 w/sf | 0.70 w/sf | 0.70 w/sf
|  |  | Pedestrian tunnels | 0.15 w/sf | 0.12 w/sf | 0.12 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 20 w/lin ft of Door Width | 14 w/lin ft of opening | 14 w/lin ft of opening
|  |  | Entry canopies | 0.25 w/sf | 0.25 w/sf | 0.25 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.60 w/sf | 0.40 w/sf | 0.40 w/sf
|  |  | Outdoor open sales areas | 0.25 w/sf | 0.20 w/sf | 0.20 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 10 w/lin ft | 7 w/lin ft | 7 w/lin ft
|  | Zone 2: Non-tradable surfaces |  |  | Additional exterior lighting power allowance
|  |  | Building facades | 0.075 w/sf of gross above-grade wall area | 0.075 w/sf of gross above-grade wall area | 0.1 w/sf of façade area or 2.5 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.35 w/sf | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry
Zone 3: all other areas
Zone 3: Tradable surfaces
|  |  | Base site allowance | 750 w | 500 w | 500 w
|  |  | Uncovered parking areas and drives | 0.10 w/sf | 0.06 w/sf | 0.06 w/sf
|  |  | Walkways <10 ft wide | 0.8 w/lin ft | 0.6 w/lin ft | 0.6 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.16 w/sf | 0.11 w/sf | 0.11 w/sf
|  |  | Dining areas |  | 0.75 w/sf | 0.75 w/sf
|  |  | Stairways | 1.0 w/sf | 0.7 w/sf | 0.7 w/sf
|  |  | Pedestrian tunnels | 0.2 w/sf | 0.14 w/sf | 0.14 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 30 w/lin ft of Door Width | 21 w/lin ft of opening | 21 w/lin ft of opening
|  |  | Entry canopies | 0.4 w/sf | 0.4 w/sf | 0.4 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 0.8 w/sf | 0.6 w/sf | 0.6 w/sf
|  |  | Outdoor open sales areas | 0.5 w/sf | 0.35 w/sf | 0.35 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 10 w/lin ft | 7 w/lin ft | 7 w/lin ft
|  | Zone 3: Non tradable surfaces |  |  | Additional exterior lighting power allowance
|  |  | Building facades | 0.113 w/sf of gross above-grade wall area | 0.113 w/sf of gross above-grade wall area | 0.15 w/sf of façade area or 3.75 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry
Zone 4: high activity commercial districts in major metropolitan areas as designated by the local jurisdiction
Zone 4: Tradable surfaces
|  |  | Base site allowance | 1300 w | 900 w | 900 w
|  |  | Uncovered parking areas and drives | 0.13 w/sf | 0.08 w/sf | 0.08 w/sf
|  |  | Walkways <10 ft wide | 1.0 w/lin ft | 0.7 w/lin ft | 0.7 w/lin ft
|  |  | Walkways ≥10 ft wide, plaza areas, special feature areas | 0.2 w/sf | 0.14 w/sf | 0.14 w/sf
|  |  | Dining areas |  | 0.95 w/sf | 0.95 w/sf
|  |  | Stairways | 1.0 w/sf | 0.70 w/sf | 0.70 w/sf
|  |  | Pedestrian tunnels | 0.3 w/sf | 0.21 w/sf | 0.21 w/sf
|  |  | Landscaping |  | 0.04 w/sf | 0.04 w/sf
|  |  | Pedestrian & vehicular entrance & exits | 30 w/lin ft of Door Width | 21 w/lin ft of opening | 21 w/lin ft of opening
|  |  | Entry canopies | 0.4 w/sf | 0.4 w/sf | 0.4 w/sf
|  |  | Loading docks |  | 0.35 w/sf | 0.35 w/sf
|  |  | Sales canopies (freestanding and attached) | 1.0 w/sf | 0.7 w/sf | 0.7 w/sf
|  |  | Outdoor open sales areas | 0.7 w/sf | 0.5 w/sf | 0.5 w/sf
|  |  | Street frontage for vehicle sales lots in addition to "open area" allowance | 30 w/lin ft | 21 w/lin ft | 21 w/lin ft
|  | Zone 4: non-tradable surfaces |  |  | Additional exterior lighting power allowance
|  |  | Building facades | 0.15 w/sf of gross above-grade wall area | 0.15 w/sf of gross above-grade wall area | 0.2 w/sf of façade area or 5.0 w/lin ft façade length
|  |  | Automated teller machines & night depositories | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Uncovered entrance & gatehouse inspection stations at guarded facilities | 0.75 w/sf of covered & uncovered area | 0.50 w/sf | 0.50 w/sf
|  |  | Uncovered loading areas for law enforcement, fire, ambulance & other emergency service vehicles | 0.5 w/sf of covered & uncovered area | 0.35 w/sf | 0.35 w/sf
|  |  | Drive-up windows/doors | 400 w per drive-through | 200 w per drive-through | 200 w per drive-through
|  |  | Parking near 24-hour retail entrances | 800 w per main entry | 400 w per main entry | 400 w per main entry
Other Equipment
Minimum Nominal Efficiency for Motors
|  |  |  | 60 HZ General Purpose Electric Motors (Subtype I) | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump) | 60 HZ NEMA Design A, NEMA Design B, IEC Design N (excluding fire pump)
ODP - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77
|  |  | 1.5 | 84 | 84 | 84
|  |  | 2 | 85.5 | 85.5 | 85.5
|  |  | 3 | 85.5 | 85.5 | 85.5
|  |  | 5 | 86.5 | 86.5 | 86.5
|  |  | 7.5 | 88.5 | 88.5 | 88.5
|  |  | 10 | 89.5 | 89.5 | 89.5
|  |  | 15 | 90.2 | 90.2 | 90.2
|  |  | 20 | 91 | 91 | 91
|  |  | 25 | 91.7 | 91.7 | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4
|  |  | 50 | 93 | 93 | 93
|  |  | 60 | 93.6 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6
|  |  | 100 | 93.6 | 93.6 | 93.6
|  |  | 125 | 94.1 | 94.1 | 94.1
|  |  | 150 | 94.1 | 94.1 | 94.1
|  |  | 200 | 95 | 95 | 95
|  |  | 250 | 95 | 95 | 95
|  |  | 300 | 95.4 | 95.4 | 95.4
|  |  | 350 | 95.4 | 95.4 | 95.4
|  |  | 400 | 95.8 | 95.8 | 95.8
|  |  | 450 | 95.8 | 96.2 | 96.2
|  |  | 500 | 95.8 | 96.2 | 96.2
ODP - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91 | 91 | 91
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 93 | 93 | 93
|  |  | 20 | 93 | 93 | 93
|  |  | 25 | 93.6 | 93.6 | 93.6
|  |  | 30 | 94.1 | 94.1 | 94.1
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5
|  |  | 60 | 95 | 95 | 95
|  |  | 75 | 95 | 95 | 95
|  |  | 100 | 95.4 | 95.4 | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8
|  |  | 250 | 95.8 | 95.8 | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8
|  |  | 400 | 95.8 | 95.8 | 95.8
|  |  | 450 | 96.2 | 96.2 | 96.2
|  |  | 500 | 96.2 | 96.2 | 96.2
ODP - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 87.5 | 87.5 | 87.5
|  |  | 3 | 88.5 | 88.5 | 88.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 90.2 | 90.2 | 90.2
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 91.7 | 91.7 | 91.7
|  |  | 20 | 92.4 | 92.4 | 92.4
|  |  | 25 | 93 | 93 | 93
|  |  | 30 | 93.6 | 93.6 | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5
|  |  | 100 | 95 | 95 | 95
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95.4 | 95.4 | 95.4
|  |  | 200 | 95.4 | 95.4 | 95.4
|  |  | 250 | 95.4 | 95.8 | 95.8
|  |  | 300 | 95.4 | 95.8 | 95.8
|  |  | 350 | 95.4 | 95.8 | 95.8
|  |  | 400 | 95.8 | NR | NR
|  |  | 450 | 96.2 | NR | NR
|  |  | 500 | 96.2 | NR | NR
ODP - 900 rpm (hp)
|  |  | 1 |  | 75.5 | 75.5
|  |  | 1.5 |  | 77 | 77
|  |  | 2 |  | 86.5 | 86.5
|  |  | 3 |  | 87.5 | 87.5
|  |  | 5 |  | 88.5 | 88.5
|  |  | 7.5 |  | 89.5 | 89.5
|  |  | 10 |  | 90.2 | 90.2
|  |  | 15 |  | 90.2 | 90.2
|  |  | 20 |  | 91 | 91
|  |  | 25 |  | 91 | 91
|  |  | 30 |  | 91.7 | 91.7
|  |  | 40 |  | 91.7 | 91.7
|  |  | 50 |  | 92.4 | 92.4
|  |  | 60 |  | 93 | 93
|  |  | 75 |  | 94.1 | 94.1
|  |  | 100 |  | 94.1 | 94.1
|  |  | 125 |  | 94.1 | 94.1
|  |  | 150 |  | 94.1 | 94.1
|  |  | 200 |  | 94.1 | 94.1
|  |  | 250 |  | 95 | 95
TEFC - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77
|  |  | 1.5 | 84 | 84 | 84
|  |  | 2 | 85.5 | 85.5 | 85.5
|  |  | 3 | 86.5 | 86.5 | 86.5
|  |  | 5 | 88.5 | 88.5 | 88.5
|  |  | 7.5 | 89.5 | 89.5 | 89.5
|  |  | 10 | 90.2 | 90.2 | 90.2
|  |  | 15 | 91 | 91 | 91
|  |  | 20 | 91 | 91 | 91
|  |  | 25 | 91.7 | 91.7 | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4
|  |  | 50 | 93 | 93 | 93
|  |  | 60 | 93.6 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6
|  |  | 100 | 94.1 | 94.1 | 94.1
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95 | 95 | 95
|  |  | 200 | 95.4 | 95.4 | 95.4
|  |  | 250 | 95.8 | 95.8 | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8
|  |  | 400 | 95.8 | 95.8 | 95.8
|  |  | 450 | 95.8 | 95.8 | 95.8
|  |  | 500 | 95.8 | 95.8 | 95.8
TEFC - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91.7 | 91.7 | 91.7
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 92.4 | 92.4 | 92.4
|  |  | 20 | 93 | 93 | 93
|  |  | 25 | 93.6 | 93.6 | 93.6
|  |  | 30 | 93.6 | 93.6 | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5
|  |  | 60 | 95 | 95 | 95
|  |  | 75 | 95.4 | 95.4 | 95.4
|  |  | 100 | 95.4 | 95.4 | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 96.2 | 96.2 | 96.2
|  |  | 250 | 96.2 | 96.2 | 96.2
|  |  | 300 | 96.2 | 96.2 | 96.2
|  |  | 350 | 96.2 | 96.2 | 96.2
|  |  | 400 | 96.2 | 96.2 | 96.2
|  |  | 450 | 96.2 | 96.2 | 96.2
|  |  | 500 | 96.2 | 96.2 | 96.2
TEFC - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5
|  |  | 1.5 | 87.5 | 87.5 | 87.5
|  |  | 2 | 88.5 | 88.5 | 88.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91 | 91 | 91
|  |  | 10 | 91 | 91 | 91
|  |  | 15 | 91.7 | 91.7 | 91.7
|  |  | 20 | 91.7 | 91.7 | 91.7
|  |  | 25 | 93 | 93 | 93
|  |  | 30 | 93 | 93 | 93
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5
|  |  | 100 | 95 | 95 | 95
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8
|  |  | 250 | 95.8 | 95.8 | 95.8
|  |  | 300 | 95.8 | 95.8 | 95.8
|  |  | 350 | 95.8 | 95.8 | 95.8
|  |  | 400 | 95.8 | NR | NR
|  |  | 450 | 95.8 | NR | NR
|  |  | 500 | 95.8 | NR | NR
TEFC - 900 rpm (hp)
|  |  | 1 |  | 75.5 | 75.5
|  |  | 1.5 |  | 78.5 | 78.5
|  |  | 2 |  | 84 | 84
|  |  | 3 |  | 85.5 | 85.5
|  |  | 5 |  | 86.5 | 86.5
|  |  | 7.5 |  | 86.5 | 86.5
|  |  | 10 |  | 89.5 | 89.5
|  |  | 15 |  | 89.5 | 89.5
|  |  | 20 |  | 90.2 | 90.2
|  |  | 25 |  | 90.2 | 90.2
|  |  | 30 |  | 91.7 | 91.7
|  |  | 40 |  | 91.7 | 91.7
|  |  | 50 |  | 92.4 | 92.4
|  |  | 60 |  | 92.4 | 92.4
|  |  | 75 |  | 93.6 | 93.6
|  |  | 100 |  | 93.6 | 93.6
|  |  | 125 |  | 94.1 | 94.1
|  |  | 150 |  | 94.1 | 94.1
|  |  | 200 |  | 94.5 | 94.5
|  |  | 250 |  | 95 | 95
|  |  |  | General Purpose Electric Motors (Subtype II and Design B) | 60 Hz NEMA Design C and IEC Design H Motors | 60 Hz NEMA Design C and IEC Design H Motors
ODP - 3600 rpm (hp)
|  |  | 1 | NR
|  |  | 1.5 | 82.5
|  |  | 2 | 84
|  |  | 3 | 84
|  |  | 5 | 85.5
|  |  | 7.5 | 87.5
|  |  | 10 | 88.5
|  |  | 15 | 89.5
|  |  | 20 | 90.2
|  |  | 25 | 91
|  |  | 30 | 91
|  |  | 40 | 91.7
|  |  | 50 | 92.4
|  |  | 60 | 93
|  |  | 75 | 93
|  |  | 100 | 93
|  |  | 125 | 93.6
|  |  | 150 | 93.6
|  |  | 200 | 94.5
|  |  | 250 | 94.5
|  |  | 300 | 95
|  |  | 350 | 95
|  |  | 400 | 95.4
|  |  | 450 | 95.8
|  |  | 500 | 95.8
ODP - 1800 rpm (hp)
|  |  | 1 | 82.5 | 85.5 | 85.5
|  |  | 1.5 | 84 | 86.5 | 86.5
|  |  | 2 | 84 | 86.5 | 86.5
|  |  | 3 | 86.5 | 89.5 | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5
|  |  | 7.5 | 88.5 | 91 | 91
|  |  | 10 | 89.5 | 91.7 | 91.7
|  |  | 15 | 91 | 93 | 93
|  |  | 20 | 91 | 93 | 93
|  |  | 25 | 91.7 | 93.6 | 93.6
|  |  | 30 | 92.4 | 94.1 | 94.1
|  |  | 40 | 93 | 94.1 | 94.1
|  |  | 50 | 93 | 94.5 | 94.5
|  |  | 60 | 93.6 | 95 | 95
|  |  | 75 | 94.1 | 95 | 95
|  |  | 100 | 94.1 | 95.4 | 95.4
|  |  | 125 | 94.5 | 95.4 | 95.4
|  |  | 150 | 95 | 95.8 | 95.8
|  |  | 200 | 95 | 95.8 | 95.8
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.8
|  |  | 500 | 95.8
ODP - 1200 rpm (hp)
|  |  | 1 | 80 | 82.5 | 82.5
|  |  | 1.5 | 84 | 86.5 | 86.5
|  |  | 2 | 85.5 | 87.5 | 87.5
|  |  | 3 | 86.5 | 88.5 | 88.5
|  |  | 5 | 87.5 | 89.5 | 89.5
|  |  | 7.5 | 88.5 | 90.2 | 90.2
|  |  | 10 | 90.2 | 91.7 | 91.7
|  |  | 15 | 90.2 | 91.7 | 91.7
|  |  | 20 | 91 | 92.4 | 92.4
|  |  | 25 | 91.7 | 93 | 93
|  |  | 30 | 92.4 | 93.6 | 93.6
|  |  | 40 | 93 | 94.1 | 94.1
|  |  | 50 | 93 | 94.1 | 94.1
|  |  | 60 | 93.6 | 94.5 | 94.5
|  |  | 75 | 93.6 | 94.5 | 94.5
|  |  | 100 | 94.1 | 95 | 95
|  |  | 125 | 94.1 | 95 | 95
|  |  | 150 | 94.5 | 95.4 | 95.4
|  |  | 200 | 94.5 | 95.4 | 95.4
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
ODP - 900 rpm (hp)
|  |  | 1 | 74 | 75.5 | 75.5
|  |  | 1.5 | 75.5 | 77 | 77
|  |  | 2 | 85.5 | 86.5 | 86.5
|  |  | 3 | 86.5 | 87.5 | 87.5
|  |  | 5 | 87.5 | 88.5 | 88.5
|  |  | 7.5 | 88.5 | 89.5 | 89.5
|  |  | 10 | 89.5 | 90.2 | 90.2
|  |  | 15 | 89.5 | 90.2 | 90.2
|  |  | 20 | 90.2 | 91 | 91
|  |  | 25 | 90.2 | 91 | 91
|  |  | 30 | 91 | 91.7 | 91.7
|  |  | 40 | 91 | 91.7 | 91.7
|  |  | 50 | 91.7 | 92.4 | 92.4
|  |  | 60 | 92.4 | 93 | 93
|  |  | 75 | 93.6 | 94.1 | 94.1
|  |  | 100 | 93.6 | 94.1 | 94.1
|  |  | 125 | 93.6 | 94.1 | 94.1
|  |  | 150 | 93.6 | 94.1 | 94.1
|  |  | 200 | 93.6 | 94.1 | 94.1
|  |  | 250 | 94.5
|  |  | 300 | NR
|  |  | 350 | NR
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
TEFC - 3600 rpm (hp)
|  |  | 1 | 75.5
|  |  | 1.5 | 82.5
|  |  | 2 | 84
|  |  | 3 | 85.5
|  |  | 5 | 87.5
|  |  | 7.5 | 88.5
|  |  | 10 | 89.5
|  |  | 15 | 90.2
|  |  | 20 | 90.2
|  |  | 25 | 91
|  |  | 30 | 91
|  |  | 40 | 91.7
|  |  | 50 | 92.4
|  |  | 60 | 93
|  |  | 75 | 93
|  |  | 100 | 93.6
|  |  | 125 | 94.5
|  |  | 150 | 94.5
|  |  | 200 | 95
|  |  | 250 | 95.4
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.4
|  |  | 500 | 95.4
TEFC - 1800 rpm (hp)
|  |  | 1 | 82.5 | 85.5 | 85.5
|  |  | 1.5 | 84 | 86.5 | 86.5
|  |  | 2 | 84 | 86.5 | 86.5
|  |  | 3 | 87.5 | 89.5 | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5
|  |  | 7.5 | 89.5 | 91.7 | 91.7
|  |  | 10 | 89.5 | 91.7 | 91.7
|  |  | 15 | 91 | 92.4 | 92.4
|  |  | 20 | 91 | 93 | 93
|  |  | 25 | 92.4 | 93.6 | 93.6
|  |  | 30 | 92.4 | 93.6 | 93.6
|  |  | 40 | 93 | 94.1 | 94.1
|  |  | 50 | 93 | 94.5 | 94.5
|  |  | 60 | 93.6 | 95 | 95
|  |  | 75 | 94.1 | 95.4 | 95.4
|  |  | 100 | 94.5 | 95.4 | 95.4
|  |  | 125 | 94.5 | 95.4 | 95.4
|  |  | 150 | 95 | 95.8 | 95.8
|  |  | 200 | 95 | 96.2 | 96.2
|  |  | 250 | 95
|  |  | 300 | 95.4
|  |  | 350 | 95.4
|  |  | 400 | 95.4
|  |  | 450 | 95.4
|  |  | 500 | 95.8
TEFC - 1200 rpm (hp)
|  |  | 1 | 80 | 82.5 | 82.5
|  |  | 1.5 | 85.5 | 87.5 | 87.5
|  |  | 2 | 86.5 | 88.5 | 88.5
|  |  | 3 | 87.5 | 89.5 | 89.5
|  |  | 5 | 87.5 | 89.5 | 89.5
|  |  | 7.5 | 89.5 | 91 | 91
|  |  | 10 | 89.5 | 91 | 91
|  |  | 15 | 90.2 | 91.7 | 91.7
|  |  | 20 | 90.2 | 91.7 | 91.7
|  |  | 25 | 91.7 | 93 | 93
|  |  | 30 | 91.7 | 93 | 93
|  |  | 40 | 93 | 94.1 | 94.1
|  |  | 50 | 93 | 94.1 | 94.1
|  |  | 60 | 93.6 | 94.5 | 94.5
|  |  | 75 | 93.6 | 94.5 | 94.5
|  |  | 100 | 94.1 | 95 | 95
|  |  | 125 | 94.1 | 95 | 95
|  |  | 150 | 95 | 95.8 | 95.8
|  |  | 200 | 95 | 95.8 | 95.8
|  |  | 250 | 95
|  |  | 300 | 95
|  |  | 350 | 95
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
TEFC - 900 rpm (hp)
|  |  | 1 | 74 | 75.5 | 75.5
|  |  | 1.5 | 77 | 78.5 | 78.5
|  |  | 2 | 82.5 | 84 | 84
|  |  | 3 | 84 | 85.5 | 85.5
|  |  | 5 | 84 | 86.5 | 86.5
|  |  | 7.5 | 85.5 | 86.5 | 86.5
|  |  | 10 | 88.5 | 89.5 | 89.5
|  |  | 15 | 88.5 | 89.5 | 89.5
|  |  | 20 | 89.5 | 90.2 | 90.2
|  |  | 25 | 89.5 | 90.2 | 90.2
|  |  | 30 | 91 | 91.7 | 91.7
|  |  | 40 | 91 | 91.7 | 91.7
|  |  | 50 | 91.7 | 92.4 | 92.4
|  |  | 60 | 91.7 | 92.4 | 92.4
|  |  | 75 | 93 | 93.6 | 93.6
|  |  | 100 | 93 | 93.6 | 93.6
|  |  | 125 | 93.6 | 94.1 | 94.1
|  |  | 150 | 93.6 | 94.1 | 94.1
|  |  | 200 | 94.1 | 94.5 | 94.5
|  |  | 250 | 94.5
|  |  | 300 | NR
|  |  | 350 | NR
|  |  | 400 | NR
|  |  | 450 | NR
|  |  | 500 | NR
|  |  |  | Polyphase Small Electric Motors | Polyphase Small Electric Motors | Polyphase Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 | 65.6 | 65.6 | 65.6
|  |  | 0.33 | 69.5 | 69.5 | 69.5
|  |  | 0.5 | 73.4 | 73.4 | 73.4
|  |  | 0.75 | 76.8 | 76.8 | 76.8
|  |  | 1 | 77 | 77 | 77
|  |  | 1.5 | 84 | 84 | 84
|  |  | 2 | 85.5 | 85.5 | 85.5
|  |  | 3 | 85.5 | 85.5 | 85.5
Open Motor - 1800 rpm (hp)
|  |  | 0.25 | 69.5 | 69.5 | 69.5
|  |  | 0.33 | 73.4 | 73.4 | 73.4
|  |  | 0.5 | 78.2 | 78.2 | 78.2
|  |  | 0.75 | 81.1 | 81.1 | 81.1
|  |  | 1 | 83.5 | 83.5 | 83.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5
|  |  | 3 | 86.9 | 86.9 | 86.9
Open Motor - 1200 rpm (hp)
|  |  | 0.25 | 67.5 | 67.5 | 67.5
|  |  | 0.33 | 71.4 | 71.4 | 71.4
|  |  | 0.5 | 75.3 | 75.3 | 75.3
|  |  | 0.75 | 81.7 | 81.7 | 81.7
|  |  | 1 | 82.5 | 82.5 | 82.5
|  |  | 1.5 | 83.8 | 83.8 | 83.8
|  |  | 2 | N/A | N/A | N/A
|  |  | 3 | N/A | N/A | N/A
|  |  |  | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 | 66.6 | 66.6 | 66.6
|  |  | 0.33 | 70.5 | 70.5 | 70.5
|  |  | 0.5 | 72.4 | 72.4 | 72.4
|  |  | 0.75 | 76.2 | 76.2 | 76.2
|  |  | 1 | 80.4 | 80.4 | 80.4
|  |  | 1.5 | 81.5 | 81.5 | 81.5
|  |  | 2 | 82.9 | 82.9 | 82.9
|  |  | 3 | 84.1 | 84.1 | 84.1
Open Motor - 1800 rpm (hp)
|  |  | 0.25 | 68.5 | 68.5 | 68.5
|  |  | 0.33 | 72.4 | 72.4 | 72.4
|  |  | 0.5 | 76.2 | 76.2 | 76.2
|  |  | 0.75 | 81.8 | 81.8 | 81.8
|  |  | 1 | 82.6 | 82.6 | 82.6
|  |  | 1.5 | 83.8 | 83.8 | 83.8
|  |  | 2 | 84.5 | 84.5 | 84.5
|  |  | 3 | N/A | N/A | N/A
Open Motor - 1200 rpm (hp)
|  |  | 0.25 | 62.2 | 62.2 | 62.2
|  |  | 0.33 | 66.6 | 66.6 | 66.6
|  |  | 0.5 | 76.2 | 76.2 | 76.2
|  |  | 0.75 | 80.2 | 80.2 | 80.2
|  |  | 1 | 81.1 | 81.1 | 81.1
|  |  | 1.5 | N/A | N/A | N/A
|  |  | 2 | N/A | N/A | N/A
|  |  | 3 | N/A | N/A | N/A
| Fire Pump Electric Motor Efficiency |  |  |  |  | See Table 10.8-6
|  |  | 1 to 500 hp |  |  | Generally lower efficiencies
Vertical and Horizontal Transportation Systems and Equipment
Elevator cabs
|  |  | Luminaires in each cab | Sum of lumens divided by sum of watts ≥35 | Sum of lumens divided by sum of watts ≥35 | Sum of lumens divided by sum of watts ≥35
|  |  | Cab ventilation power | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm
|  |  | Cab standby control | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes
Escalators and moving walks
|  |  | Automatic controls | To reduce speed to minimum permitted speed when not conveying passengers | To reduce speed to minimum permitted speed when not conveying passengers | To reduce speed to minimum permitted speed when not conveying passengers
Escalators
|  |  | Designed for one-way down operation or for reverse operation | Have variable frequency regenerative drive that supplies electrical energy to building electrical system when combined weight of passengers ≥750 pounds | Have variable frequency regenerative drive that supplies electrical energy to building electrical system when combined weight of passengers ≥750 pounds
| Service Water Pressure Booster Systems |  |  |  |  | Designed such that:
Pressure sensors vary speed or start/stop pumps;
No device to reduce water supply pressure;
No booster pump operation when no flow
Whole-Building Energy Monitoring
Monitoring
|  |  | Measurement device for energy use supplied by utility, energy provider or plant not within building |  |  | Natural gas
Fuel oil
Propane
Steam
Chilled water
Hot water
Recording and reporting
|  |  | Recorded |  |  | At least every 60 minutes
|  |  | Reported |  |  | Hourly
|  |  | (and with capability to create user reports) |  |  | Daily
Monthly
Annually
|  |  | Retained |  |  | ≥36 months
Exceptions
Buildings or additions <25,000 sf
Individual tenant spaces <10,000 sf
Dwelling units
Residential buildings with common areas <10,000 sf
Fuel for on-site emergency equipment
Additional Efficiency Package Options (Section C406)
Comply with at least one of the following:
|  |  | More efficient HVAC performance | Equipment shall exceed minimum efficiency requirements by ≥10% in addition to requirements listed for Section C403 | Equipment shall exceed minimum efficiency requirements by ≥10% in addition to requirements listed for Section C403
|  |  |  | Where multiple performance requirements are listed, equipment shall exceed all requirements by ≥10% | Where multiple performance requirements are listed, equipment shall exceed all requirements by ≥10%
|  |  |  | Equipment not listed shall be ≤10% of total building system capacity | Equipment not listed shall be ≤10% of total building system capacity
|  |  | Reduced lighting power density | Total interior lighting power of building <90% of lighting power calculated using building area method or space-by-space method | Total interior lighting power of building <90% of lighting power calculated using building area method or space-by-space method
|  |  | Enhanced lighting controls | Interior lighting shall have following enhanced controls located, scheduled and operated in accordance with Section C405.2.2: | Interior lighting shall have following enhanced controls located, scheduled and operated in accordance with Section C405.2.2:
|  |  |  | 1) Luminaires capable of continuous dimming | 1) Luminaires capable of continuous dimming
|  |  |  | 2) Luminaires capable of being addressed individually. Where luminaire class type is not available, controlled group ≤4 luminaires is allowed | 2) Luminaires capable of being addressed individually. Where luminaire class type is not available, controlled group ≤4 luminaires is allowed
|  |  |  | 3) ≤8 luminaires controlled together in a daylight zone | 3) ≤8 luminaires controlled together in a daylight zone
|  |  |  | 4) Fixtures controlled through digital control system that includes: | 4) Fixtures controlled through digital control system that includes:
|  |  |  | 4.1) Control reconfiguration based on digital addressability | 4.1) Control reconfiguration based on digital addressability
|  |  |  | 4.2) Load shedding | 4.2) Load shedding
|  |  |  | 4.3) Individual user control of overhead general illumination in open office | 4.3) Individual user control of overhead general illumination in open office
|  |  |  | 4.4) Occupancy sensors capable of being reconfigured through digital control system | 4.4) Occupancy sensors capable of being reconfigured through digital control system
|  |  |  | 5) Construction documents include submittal of Sequence of Operations, including specifications outlining each function in Item 4 | 5) Construction documents include submittal of Sequence of Operations, including specifications outlining each function in Item 4
|  |  |  | 6) Functional testing of lighting controls per Section C408 | 6) Functional testing of lighting controls per Section C408
|  |  | On-site supply of renewable energy | Total minimum ratings comply with one of: | Total minimum ratings comply with one of:
|  |  |  | ≥0.5 w/sf of Conditioned Floor Area | ≥1.71 Btu/h or ≥0.5 w/sf of conditioned floor area
|  |  |  | ≥3% energy used for mechanical, service water heating and lighting within building | ≥3% energy used for mechanical, service water heating and lighting within building
|  |  | Dedicated outdoor air system for certain HVAC equipment | Independent ventilation system designed to provide ≥100% outdoor air to each individual occupied space as specified by IMC | Independent ventilation system designed to provide ≥100% outdoor air to each individual occupied space as specified by IMC
|  |  |  | Ventilation system capable of total energy recovery | Ventilation system capable of total energy recovery
|  |  |  | Automatic controls for supply-air temperature reset | Automatic controls for supply-air temperature reset
|  |  | Reduced energy use service water heating | Following building types to use this compliance method: | Following building types to use this compliance method:
|  |  |  | Group R-1: Boarding house, hotels or motels | Group R-1: Boarding house, hotels or motels
|  |  |  | Group I-2: Hospitals, psychiatric hospitals & nursing homes | Group I-2: Hospitals, psychiatric hospitals & nursing homes
|  |  |  | Group A-2: Restaurants and banquet halls or buildings containing food preparation areas | Group A-2: Restaurants and banquet halls or buildings containing food preparation areas
|  |  |  | Group F: Laundries | Group F: Laundries
|  |  |  | Group R-2: Buildings with residential occupancies | Group R-2: Buildings with residential occupancies
|  |  |  | Group A-3: Health club & spas | Group A-3: Health club & spas
|  |  |  | Buildings showing service hot water load ≥10% total building energy load | Buildings showing service hot water load ≥10% total building energy load
|  |  |  | One or more of following to provide ≥60% hot water requirements or sized to provide 100% hot water requirements: | One or more of following to provide ≥60% hot water requirements or sized to provide 100% hot water requirements:
|  |  |  | 1) Waste heat recovery | 1) Waste heat recovery
|  |  |  | 2) Solar water-heating system | 2) Solar water-heating system
|  |  | Enhanced envelope performance |  | Designed building total UA ≤85% total UA of code compliant building
|  |  | Reduced air infiltration |  | Verified by whole-building pressurization test conducted by independent third party
≤0.25 cfm/sf air-leakage rate of whole above- & below-grade building envelope @ 0.3"
Exceptions:
Allowed on representative sections ≥25% conditioned floor area for building >250,000 sf
Alternate Compliance |  |  |  | Total Building Performance | Total Building Performance | Energy Cost Budget Method
|  |  |  | Section C407 | Section C407 | Section 11
or
Appendix G
System Commissioning |  |  |  | Section C408 | Section C408 | From each section for
Building operations & maintenance information
Information provided to owner
Manufacturers' information, specifications & recommendations
Programming procedures & data points
Narratives
Other illustrative means
Required regular maintenance actions posted on labels
Building envelope inspection and verification
|  |  | Inspections |  |  | Fenestration & door requirements
Loading dock weatherseals
Opaque envelope air tightness requirements
Fenestration
|  |  | Verification |  |  | Building envelope
Air leakage per one of:
a) Air barrier design & installation
b) Whole-building pressurization testing
| Mechanical systems and service water-heating systems commissioning and completion requirements |  |  |  |  | Submittals & completion requirements
|  |  |  | Construction documents clearly indicate provisions for commissioning and completion requirements | Construction documents clearly indicate provisions for commissioning and completion requirements | Construction documents shall require HVAC control systems to be tested to ensure control elements are calibrated, adjusted and in proper working conditions for projects >50,000 sf conditioned area except for warehouses & semi-heated spaces
|  |  |  | Provide evidence of commissioning and completion prior to final inspection | Provide evidence of commissioning and completion prior to final inspection
|  |  |  | Copies of all documentation given to owner and made available to code official | Copies of all documentation given to owner and made available to code official
|  |  |  | Exceptions: | Exceptions: | Authority having jurisdiction may require compliance documentation and supplemental information
|  |  |  | 1) Mechanical systems in buildings where total mechanical equipment capacity ≤480,000 Btu/h cooling capacity and ≤600,000 Btu/h heating capacity | 1) Mechanical systems in buildings where total mechanical equipment capacity ≤480,000 Btu/h cooling capacity and ≤600,000 Btu/h heating capacity
|  |  |  | 2) Systems serving individual dwelling units and sleeping units | 2) Systems serving individual dwelling units and sleeping units
Commissioning plan
|  |  |  | Narrative description of activities during each phase including personnel to accomplish each | Narrative description of activities during each phase including personnel to accomplish each | ASHRAE Guideline 1.1-2007, HVAC&R Technical Requirements for the Commissioning Process
|  |  |  | Specific equipment, appliances or systems to be tested and description of test | Specific equipment, appliances or systems to be tested and description of test
|  |  |  | Functions to be tested, including but not limited to calibration and economizer controls | Functions to be tested, including but not limited to calibration and economizer controls
|  |  |  | Conditions under which test will be performed | Conditions under which test will be performed
|  |  |  | Measurable criteria for performance | Measurable criteria for performance
Systems adjusting and balancing
|  |  | Air systems balancing | Required | Required
|  |  |  | Discharge dampers used for balancing prohibited on fans ≥10 hp | Discharge dampers used for balancing prohibited on fans ≥10 hp
|  |  |  | Speed adjusted on fans >1 hp | Speed adjusted on fans >1 hp
|  |  | Hydronic systems balancing | Required | Required
|  |  |  | Exceptions: | Exceptions:
|  |  |  | 1) Pump motors ≤5 hp | 1) Pump motors ≤5 hp
|  |  |  | 2) When throttling results ≤5% nameplate hp draw above that if impeller were trimmed | 2) When throttling results ≤5% nameplate hp draw above that if impeller were trimmed
Functional performance testing
|  |  | Equipment | Demonstrate installation and operation of components, systems and system-to-system interfacing relationships | Demonstrate installation and operation of components, systems and system-to-system interfacing relationships
|  |  |  | All modes in sequence of operation | All modes in sequence of operation
|  |  |  | Redundant or automatic back-up mode | Redundant or automatic back-up mode
|  |  |  | Alarm performance | Alarm performance
|  |  |  | Mode of operation upon loss and restoration of power | Mode of operation upon loss and restoration of power
|  |  |  | Exception: unitary or packaged equipment not required to have supply air economizers | Exception: unitary or packaged equipment not required to have supply air economizers
|  |  | Controls | Document that control devices, components, equipment and systems are calibrated, adjusted and operational | Document that control devices, components, equipment and systems are calibrated, adjusted and operational
|  |  |  | Determine air economizers operate | Determine air economizers operate
|  | Preliminary commissioning report |  | Completed and provided to owner | Completed and provided to owner
|  |  |  | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections
|  |  |  | Itemize deficiencies found but not corrected at time of report | Itemize deficiencies found but not corrected at time of report
|  |  |  | Identify deferred tests that could not be performed because of climate conditions | Identify deferred tests that could not be performed because of climate conditions
|  |  |  | Climate conditions required for deferred tests | Climate conditions required for deferred tests
|  |  |  | Results of functional performance tests | Results of functional performance tests
|  |  |  | Functional performance test procedures | Functional performance test procedures
|  |  |  | Letter from owner to code official acknowledging receipt of report prior to final inspection | Copy of report given to code official by owner prior to final inspection
|  |  |  | Code official permitted to require a copy for review | Code official permitted to have report made available for review
|  | Documentation requirements |  | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal of record drawings within 90 days of system acceptance
|  |  | Drawings | Location and performance data of each piece of equipment requiring maintenance |  | Location and performance data of each piece of equipment requiring maintenance
General configuration of duct & pipe distribution system, including sizes
Terminal air or water design flow rates
|  |  | Manuals (operating manual and maintenance manual) | Submittal data for each piece of equipment requiring maintenance |  | Submittal data for each piece of equipment requiring maintenance
|  |  |  | Manufacturer's operation manuals and maintenance manuals for each piece of equipment requiring maintenance |  | Manufacturer's operation manuals and maintenance manuals for each piece of equipment requiring maintenance
|  |  |  | Name and address of service agency |  | Name and address of service agency
|  |  |  | Control system maintenance and calibration information including wiring diagrams, schematics and control sequence descriptions |  | Control system maintenance and calibration information including wiring diagrams, schematics and control sequence descriptions
|  |  |  | Desired or field-determined set points |  | Desired or field-determined set points
|  |  |  | Narrative of how each system is intended to operate |  | Narrative of how each system is intended to operate
|  |  | System balancing report | Written report describing activities and measurements | Written report describing activities and measurements | Written report for HVAC systems serving zones with total conditioned area >5,000 sf
|  | Final commissioning report |  | Completed and provided to owner | Completed and provided to owner
|  |  |  | Mechanical and service hot water findings in separate sections | Mechanical and service hot water findings in separate sections
|  |  |  | Results of functional performance tests | Results of functional performance tests
|  |  |  | Disposition of deficiencies found during testing including details of corrective measures used or proposed | Disposition of deficiencies found during testing including details of corrective measures used or proposed
|  |  |  | Functional performance test procedures including measurable criteria for test acceptance | Functional performance test procedures including measurable criteria for test acceptance
|  |  |  | Exception: Deferred tests that could not be performed at time of report preparation due to climate conditions | Exception: Deferred tests that could not be performed at time of report preparation due to climate conditions
| Power commissioning and completion requirements |  |  |  |  | Submittals
|  |  | Drawings |  |  | Construction documents to require submittal of record drawings within 30 days of system acceptance
Single-line diagram of building electrical distribution system
Location and area served for all distribution
|  |  | Manuals (operating manual and maintenance manual) |  |  | Submittal data for each piece of equipment requiring maintenance
Operation manuals and maintenance manuals for each piece of equipment requiring maintenance with routine maintenance actions clearly identified
Name and address of service agency
Narrative of how each system is intended to operate
| Lighting systems commissioning and completion requirements |  |  |  |  | Submittals - Completion Requirements
|  | Documentation requirements |  | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal within 90 days of Certificate of Occupancy | Construction documents to require submittal of record drawings within 90 days of system acceptance
Design documents to identify all luminaires for general lighting located within:
Daylight areas under skylights
Daylight areas under roof monitors
Primary sidelighted areas
Secondary sidelighted areas
|  |  | Drawings |  | Location & catalog number of each piece of equipment | Location, luminaire identifier, control and circuiting for each piece of lighting equipment
Identification of all luminaires for general lighting in daylight zones
|  |  | Manuals | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls |  | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls
|  |  |  | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions, cleaning and recommended relamping | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions, cleaning and recommended relamping | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions and recommended relamping/cleaning program
|  |  |  | Inspection and recalibration schedules for all lighting controls | Inspection and recalibration schedules for all lighting controls | Inspection and recalibration schedules for all lighting controls
|  |  |  | Narrative of how each system is intended to operate including recommended settings | Narrative of how each system is intended to operate including recommended settings | Narrative of how each system is intended to operate including recommended settings
|  | Functional testing |  | Provide evidence of commissioning prior to final inspection | Provide evidence of commissioning prior to final inspection | Control devices & systems tested to ensure control hardware & software are calibrated, adjusted, programmed & in proper working condition
|  |  | Occupant sensor controls | Certify that sensors have been located and aimed | Certify that sensors have been located and aimed | Certify that sensors have been located and aimed
|  |  |  | Test all sensors for projects with ≤7 sensors | Test all sensors for projects with ≤7 sensors | Test all sensors for projects with ≤7 sensors
|  |  |  | For projects with >7 sensors, test each unique combination of sensor type and space geometry | For projects with >7 sensors, test each unique combination of sensor type and space geometry | For projects with >7 sensors, test each unique combination of sensor type and space geometry
|  |  |  | Test ≥10% of each combination | Test ≥10% of each combination
|  |  |  | Where ≥30% controls fail, test all of identical combination | Where ≥30% controls fail, test all of identical combination
|  |  |  | Test to verify | Test to verify | Test to verify
|  |  |  | 1) Status indicator operation | 1) Status indicator operation | 1) Status indicator operation
|  |  |  | 2) Turn off or down to permitted level within required time | 2) Turn off or down to permitted level within required time | 2) Turn off or down to permitted level within required time
|  |  |  | 3) Auto-on to permitted level | 3) Auto-on to permitted level | 3) Auto-on to permitted level
|  |  |  | 4) Manual-on function | 4) Manual-on function | 4) Manual-on function
|  |  |  | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation
|  |  | Time-switch controls | Confirm accurate programming for weekday, weekend and holiday schedules | Confirm accurate programming for weekday, weekend and holiday schedules | Confirm accurate programming for weekday, weekend and holiday schedules
|  |  |  | Provide documentation to owner of programming | Provide documentation to owner of programming | Provide documentation to owner of programming
|  |  |  | Verify correct time and date | Verify correct time and date | Verify correct time and date
|  |  |  | Verify any battery back-up is installed and energized | Verify any battery back-up is installed and energized | Verify any battery back-up is installed and energized
|  |  |  | Verify override time limit ≤2 hours | Verify override time limit ≤2 hours | Verify override time limit ≤2 hours
|  |  |  | Simulate occupied condition | Simulate occupied condition | Simulate occupied condition
|  |  |  | 1) All lights operated by respective area control switch | 1) All lights operated by respective area control switch | 1) All lights operated by respective area control switch
|  |  |  | 2) Switch only operates lighting in enclosed space in which located | 2) Switch only operates lighting in enclosed space in which located | 2) Switch only operates lighting in enclosed space in which located
|  |  |  | Simulate unoccupied condition | Simulate unoccupied condition | Simulate unoccupied condition
|  |  |  | 1) Nonexempt lighting turns off | 1) Nonexempt lighting turns off | 1) Nonexempt lighting turns off
|  |  |  | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs
|  |  | Daylight responsive controls | Verify devices proper location, calibration and accurate setpoints and threshold light levels | Verify devices proper location, calibration and accurate setpoints and threshold light levels | Verify devices proper location, calibration and accurate setpoints and threshold light levels
|  |  |  | Verify lighting load adjustments in response to available daylight | Verify lighting load adjustments in response to available daylight | Verify lighting load adjustments in response to available daylight
|  |  |  | Locations of equipment adjustment are readily accessible only to authorized personnel | Locations of equipment adjustment are readily accessible only to authorized personnel | Locations of equipment adjustment are readily accessible only to authorized personnel

## Residential
Comparison of Residential Building Performance Characteristics Between |  |  |  | Residential | Residential
2015 and 2018 International Energy Conservation Code |  |  |  | Provisions | Provisions
For Climate Zone 5A |  |  |  | 2015 IECC | 2018 IECC
Administration
| Intent and Scope |  |  | Regulate the design and construction of buildings for effective use and conservation of energy over useful life of each building | Regulate the design and construction of buildings for effective use and conservation of energy over useful life of each building
|  |  |  | Applies to residential buildings and buildings sites and associated systems and equipment | Applies to residential buildings and buildings sites and associated systems and equipment
| Applicability / Compliance |  |  | Project shall comply with one of: | Project shall comply with one of:
|  |  |  | 1) This code | 1) This code
|  |  |  | 2) Simulated performance alternative plus mandatory requirements of this code | 2) Simulated performance alternative plus mandatory requirements of this code
|  |  |  | 3) Energy rating index (ERI) approach | 3) Energy rating index (ERI) approach
|  |  | Additions | In existing building section | In existing building section
|  |  | Alterations | In existing building section | In existing building section
|  |  | Change of occupancy | In existing building section | In existing building section
|  |  | Change in space conditioning | In existing building section | In existing building section
Certificate (Mandatory)
| Completed certificate |  |  | Posted on wall in space near furnace, utility room or approved location | Posted on wall in space near furnace, utility room or approved location
|  |  |  | Where located on electrical panel, certificate not to cover or obstruct visibility of circuit directory or other required labels | Where located on electrical panel, certificate not to cover or obstruct visibility of circuit directory or other required labels
Building Envelope |  |  |  | Zone 5A | Zone 5A
Insulation and fenestration requirements by component
|  |  | Fenestration U-factor | 0.32 | 0.3
|  |  | Skylight U-factor | 0.55 | 0.55
|  |  | Glazed fenestration SHGC | NR | NR
|  |  | Ceiling R-value | 49 | 49
|  |  | Wood frame wall R-value | 20 or 13 + 5 | 20 or 13 + 5
|  |  | Mass wall R-value | 13/17 | 13/17
|  |  | Floor R-value | 30 | 30
|  |  | Basement wall R-value | 15/19 | 15/19
|  |  | Slab R-value & depth (unheated) | 10, 2 ft | 10, 2 ft
|  |  | Slab R-value & depth (heated) | 15, 2 ft | R-10 to bottom of slab &
R-5 under full slab
|  |  | Crawl space wall R-value | 15/19 | 15/19
U-factor alternative
|  |  | Fenestration U-factor | 0.32 | 0.3
|  |  | Skylight U-factor | 0.55 | 0.55
|  |  | Ceiling U-factor | 0.026 | 0.026
|  |  | Frame wall U-factor | 0.06 | 0.06
|  |  | Mass wall U-factor | 0.082 | 0.082
|  |  | Floor U-factor | 0.033 | 0.033
|  |  | Basement wall U-factor | 0.05 | 0.05
|  |  | Crawl space wall U-factor | 0.055 | 0.055
Total UA alternative
|  |  | Total building envelope | Proposed UA ≤ UA using table values | Proposed UA ≤ UA using table values
Specific insulation requirements (Prescriptive)
|  | Ceilings with attic space |  | R-38 deemed to comply for R-49 wherever full height insulation extends over top plate at eaves | R-38 deemed to comply for R-49 wherever full height insulation extends over top plate at eaves
|  | Ceilings without attic space |  | R-30 that fits into roof/ceiling space and is limited to ≤500 sf or ≤20% total insulated ceiling, whichever is less | R-30 that fits into roof/ceiling space and is limited to ≤500 sf or ≤20% total insulated ceiling, whichever is less
|  | Eave baffle |  | Required for air permeable insulation in vented attic | Required for air permeable insulation in vented attic
|  | Access hatches & doors |  | Weatherstripped & insulated to equivalent insulation on surrounding surfaces | Weatherstripped & insulated to equivalent insulation on surrounding surfaces
Steel-frame assemblies
|  |  | Steel truss ceilings | R-38 + 5 | R-38 + 5
|  |  | Steel joist ceiling | R-49 in 2×4 or 2×6 or 2×8 or 2×10 | R-49 in 2×4 or 2×6 or 2×8 or 2×10
|  |  | Steel-framed wall 16" oc | R-0 + 14.0 or | R-0 + 14.0 or
|  |  |  | R-13 + 8.9 or | R-13 + 8.9 or
|  |  |  | R-15 + 8.5 or | R-15 + 8.5 or
|  |  |  | R-19 + 7.8 or | R-19 + 7.8 or
|  |  |  | R-19 + 6.2 or | R-19 + 6.2 or
|  |  |  | R-21 + 7.5 | R-21 + 7.5
|  |  | Steel-framed wall 24" oc | R-0 + 14 or | R-0 + 14 or
|  |  |  | R-13 + 7.7 or | R-13 + 7.7 or
|  |  |  | R-15 + 7.1 or | R-15 + 7.1 or
|  |  |  | R-19 + 6.3 or | R-19 + 6.3 or
|  |  |  | R-21 + 5.9 | R-21 + 5.9
|  |  | Steel joist floors | R-19 + 6 in 2×6 or | R-19 + 6 in 2×6 or
|  |  |  | R-19 12 in 2×8 or | R-19 12 in 2×8 or
|  |  |  | R-19 +12 in 2×10 | R-19 +12 in 2×10
|  | Walls with partial structural sheathing |  | Continuous insulation permitted to be reduced ≤R-3 for consistent total sheathing thickness | Continuous insulation permitted to be reduced ≤R-3 for consistent total sheathing thickness
where structural sheathing covers ≤40% gross area of all exterior walls
|  | Basement walls |  | Top of wall to 10' below grade or to basement floor | Top of wall to 10' below grade or to basement floor
|  |  |  | Unconditioned basement walls to be insulated unless floor overhead is insulated | Unconditioned basement walls to be insulated unless floor overhead is insulated
|  | Slab-on-grade floors |  | Floor surface <12" below grade | Floor surface <12" below grade
|  |  |  | Top of slab to 24" below grade by any combination of vertical & horizontal | Top of slab to 24" below grade by any combination of vertical & horizontal
|  |  |  | Extending away protected by pavement or 10" soil | Extending away protected by pavement or 10" soil
|  | Crawl space walls |  | Not vented to outside | Not vented to outside
|  |  |  | Downward from floor to finish grade level & then vertically and/or horizontally additional ≥24" | Downward from floor to finish grade level & then vertically and/or horizontally additional ≥24"
|  |  |  | Exposed earth covered by Class I vapor retarder | Exposed earth covered by Class I vapor retarder
|  | Sunroom insulation |  | Exception for thermally isolated conditioned spaces | Exception for thermally isolated conditioned spaces
|  |  |  | ≥R-24 ceiling insulation | ≥R-24 ceiling insulation
|  |  |  | ≥R-13 wall insulation | ≥R-13 wall insulation
|  |  |  | Wall(s) separating sunroom from conditioned space shall meet building thermal envelope requirement | Wall(s) separating sunroom from conditioned space shall meet building thermal envelope requirement
Fenestration (Prescriptive)
|  | U-factor |  | Area-weighted average permitted | Area-weighted average permitted
|  | Glazed fenestration exemption |  | ≤15 sf per dwelling unit exempted from U-factor requirement | ≤15 sf per dwelling unit exempted from U-factor requirement
|  | Opaque door exemption |  | One side-hinged ≤24 sf exempt from U-factor requirement | One side-hinged ≤24 sf exempt from U-factor requirement
|  | Sunroom U-factor |  | Exception for thermally isolated conditioned space | Exception for thermally isolated conditioned space
|  |  | Fenestration | ≤U-0.45 | ≤U-0.45
|  |  | Skylight | ≤U-0.70 | ≤U-0.70
|  |  | New fenestration separating sunroom from conditioned space | ≤U-0.32 | ≤U-0.30
|  | Replacement fenestration (some or all of existing fenestration) |  | ≤U-0.32 | ≤U-0.30
|  |  |  | In Existing Building Alterations Section | In Existing Building Alterations Section
Air Leakage (Mandatory)
|  | Sealing methods between dissimilar materials |  | Allow for differential expansion and contraction | Allow for differential expansion and contraction
|  | Installation |  | Per manufacturer's instructions | Per manufacturer's instructions
|  |  |  | Per air barrier and insulation installation criteria listed Table R402.4.1.1 | Per air barrier and insulation installation criteria listed Table R402.4.1.1
|  | Testing |  | Performed at any time after creation of all penetrations of thermal envelope | Performed at any time after creation of all penetrations of thermal envelope
|  |  |  | ≤3 ach | ≤3 ach
|  |  |  | Provide written report signed by party conducting test | Provide written report signed by party conducting test
|  | Fireplaces |  | New wood-burning | New wood-burning
|  |  |  | Tight-fitting flue dampers or doors | Tight-fitting flue dampers or doors
|  |  |  | Outdoor combustion air | Outdoor combustion air
Fenestration air leakage
|  |  | Windows, skylights & sliding glass doors | ≤0.3 cfm/sf | ≤0.3 cfm/sf
|  |  | Swinging doors | ≤0.5 cfm/sf | ≤0.5 cfm/sf
|  |  | Exemption: | Site-built windows, skylights & doors | Site-built windows, skylights & doors
|  | Rooms containing fuel-burning appliances |  | Where open combustion air ducts provide combustion air to open combustion fuel-burning appliances | Where open combustion air ducts provide combustion air to open combustion fuel-burning appliances
|  |  | Location of appliances and combustion air opening | Outside of building thermal envelope or | Outside of building thermal envelope or
|  |  |  | Enclosed in room isolated from inside thermal envelope | Enclosed in room isolated from inside thermal envelope
|  |  | Enclosed rooms containing fuel-burning appliances | Doors fully gasketed | Doors fully gasketed
|  |  |  | Water lines & ducts insulated | Water lines & ducts insulated
|  |  |  | ≥R-8 insulation on combustion air duct | ≥R-8 insulation on combustion air duct
|  |  |  | Insulated to envelope requirements but not less than basement wall R-value | Insulated to envelope requirements but not less than basement wall R-value
|  |  | Exceptions | Direct vent appliances with both intake and exhaust pipes to outside | Direct vent appliances with both intake and exhaust pipes to outside
|  |  |  | Code compliant fireplaces and stoves | Code compliant fireplaces and stoves
|  | Recessed lighting (in thermal envelope) |  | Sealed between housing & interior wall or ceiling covering | Sealed between housing & interior wall or ceiling covering
|  |  |  | IC-rated | IC-rated
|  |  |  | ≤2.0 cfm air leakage rate | ≤2.0 cfm air leakage rate
Maximum area-weighted average using tradeoffs (Mandatory)
|  |  | Vertical fenestration | U-0.48 | U-0.48
|  |  | Skylights | U-0.75 | U-0.75
Systems
| Controls (Mandatory) |  |  | ≥1 for each separate heating & cooling system | ≥1 for each separate heating & cooling system
|  | Programmable thermostat |  | Controls primary heating and cooling system | Controls primary heating and cooling system
|  |  |  | Capabilities: | Capabilities:
|  |  |  | Daily schedule | Daily schedule
|  |  |  | Setback or temporarily operate system | Setback or temporarily operate system
|  |  |  | Maintain zone temperature between 55°F & 85°F | Maintain zone temperature between 55°F & 85°F
|  | Heat pump supplementary electric resistance heat (Mandatory) |  | Prevent resistance heat operation when compressor can meet heating load | Prevent resistance heat operation when compressor can meet heating load
|  | Hot water boiler outdoor temperature setback |  | Supply heat to building through one- or two-pipe systems | Supply heat to building through one- or two-pipe systems
|  |  |  | Lowers water temperature based on outdoor temperature | Lowers water temperature based on outdoor temperature
Ducts
Insulation (Prescriptive)
|  |  | Supply and return ducts in ≥3" diameter in attic | ≥R-8 | ≥R-8
|  |  | Supply and return ducts in <3" diameter in attic | ≥R-6 | ≥R-6
|  |  | Supply and return ducts in ≥3" diameter in other areas | ≥R-6 | ≥R-6
|  |  | Supply and return ducts in <3" diameter in other areas | ≥R-4.2 | ≥R-4.2
|  |  | Exemption: | Ducts or portion thereof inside thermal envelope | Ducts or portion thereof inside thermal envelope
Sealing (Mandatory)
|  |  | Ducts, air handlers & filter boxes | Sealed | Sealed
Testing
|  |  | Post construction | ≤4 cfm per 100 sf of conditioned floor area across entire system | ≤4 cfm per 100 sf of conditioned floor area across entire system
|  |  | Rough-in with air handler | ≤4 cfm per 100 sf of conditioned floor area across system | ≤4 cfm per 100 sf of conditioned floor area across system
|  |  | Rough-in without air handler | ≤3 cfm per 100 sf of conditioned floor area | ≤3 cfm per 100 sf of conditioned floor area
|  |  | Exception: | Testing not required for ducts & air handlers located entirely within building thermal envelope | Testing not required for ducts & air handlers located entirely within building thermal envelope
Testing not required for heat or energy recovery ventilator ducts
|  |  | Sealed air handler | Manufacturer's designation for leakage rate ≤2% of design air flow | Manufacturer's designation for leakage rate ≤2% of design air flow
|  |  | Building cavities (Mandatory) | Framing cavities not to be used as ducts or plenums | Framing cavities not to be used as ducts or plenums
|  | Ducts buried within ceiling insulation |  |  | Partially or completely buried
≥R-8 on supply and return ducts
Sum of ceiling insulation against & above top of duct and against & below bottom of duct ≥R-19, excluding R-value of duct insulation
|  |  | Effective R-value of deeply buried ducts |  | R-25 considered effective R-value
Where using simulated energy performance analysis
Ducts located on or within 5.5" of ceiling
Surrounded by blow-in attic insulation ≥R-30 with top of insulation ≥3.5" above top of duct
|  | Ducts located in conditioned space |  |  | Comply with either to be considered
1) Completely within continuous air barrier & within building thermal envelope
2) Buried within ceiling insulation, all of following:
2.1) Air handler located completely within continuous air barrier & building thermal envelope
2.2) Total system duct leakage ≤1.5 cfm per 100 sf
2.3) R-value of ceiling insulation against & above the insulated duct ≥ R-value of ceiling insulation minus R-value of duct insulation
Mechanical system piping insulation (Mandatory)
|  | Insulation on piping capable of carrying fluids >105°F and <55°F |  | ≥R-3 | ≥R-3
|  | Insulation protection |  | From damage from sunlight, moisture, equipment maintenance and wind | From damage from sunlight, moisture, equipment maintenance and wind
|  |  |  | Shielded from solar radiation | Shielded from solar radiation
|  |  |  | Adhesive tape not permitted | Adhesive tape not permitted
Service hot water systems
Circulating hot water systems (Mandatory)
|  |  | Circulation systems | Automatic controls, temperature sensors & pump to be accessible. | Automatic controls, temperature sensors & pump to be accessible.
|  |  |  | Manual controls to be readily accessible | Manual controls to be readily accessible
|  |  |  | Provided with circulation pump | Provided with circulation pump
|  |  |  | Gravity & thermosyphon circulation systems prohibited | Gravity & thermosyphon circulation systems prohibited
|  |  |  | Controls start pump based on demand | Controls start pump based on demand
|  |  |  | Controls automatically turn off pump when loop is at desired temperature & when there is no demand | Controls automatically turn off pump when loop is at desired temperature & when there is no demand
|  |  | Heat trace systems | Controls to automatically adjust energy input to maintain desired water temperature when heated water is used in occupancy | Controls to automatically adjust energy input to maintain desired water temperature when heated water is used in occupancy
|  |  | Demand recirculation systems | Pumps heated water from supply & back to source through cold water supply pipe | Pumps heated water from supply & back to source through cold water supply pipe
|  |  |  | Controls shall: | Controls shall:
|  |  |  | 1) Start pump upon receiving signal from action of user, sensing presence of user, or sensing flow | 1) Start pump upon receiving signal from action of user, sensing presence of user, or sensing flow
|  |  |  | 2) Limit temperature entering cold water piping to 104°F | 2) Limit temperature entering cold water piping to 104°F
|  | Hot water pipe insulation (Prescriptive) |  | ≥R-3 on piping: | ≥R-3 on piping:
|  |  |  | 1) ≥¾" nominal diameter | 1) ≥¾" nominal diameter
|  |  |  | 2) Serving >1 dwelling unit | 2) Serving >1 dwelling unit
|  |  |  | 3) Located outside conditioned space | 3) Located outside conditioned space
|  |  |  | 4) From water heater to distribution manifold | 4) From water heater to distribution manifold
|  |  |  | 5) Located under floor slab | 5) Located under floor slab
|  |  |  | 6) Buried | 6) Buried
|  |  |  | 7) Supply & return in recirculating systems other than demand recirculating systems | 7) Supply & return in recirculating systems other than demand recirculating systems
Drain water heat recovery units
|  |  | Potable water-side pressure loss | <3 psi for units connected to 1 or 2 showers | <3 psi for units connected to 1 or 2 showers
|  |  |  | <2 psi for units connected to ≥3 showers | <2 psi for units connected to ≥3 showers
Mechanical ventilation (Mandatory)
|  | Dampers on outdoor air intakes & exhausts |  | Automatic or gravity that close when system not operating | Automatic or gravity that close when system not operating
Whole-house mechanical ventilation system fan efficiency
|  |  | HRV or ERV |  | 1.2 cfm/watt
|  |  | Range hoods | 2.8 cfm/watt | 2.8 cfm/watt
|  |  | In-line fan | 2.8 cfm/watt | 2.8 cfm/watt
Bathroom, utility room
|  |  | ≥10 & <90 cfm | 1.4 cfm/watt | 1.4 cfm/watt
|  |  | ≥90 cfm | 2.8 cfm/watt | 2.8 cfm/watt
|  |  | Exception: | Fans integral to tested & listed HVAC equipment | Fans integral to tested & listed HVAC equipment
|  |  |  | Air handler powered by electronically commutated motor | Air handler powered by electronically commutated motor
Equipment sizing and efficiency rating (mandatory)
|  | Equipment sizing (Mandatory) |  | Heating & cooling equipment | Heating & cooling equipment
|  |  |  | Sized in accordance with ACCA Manual S | Sized in accordance with ACCA Manual S
|  |  |  | Loads calculated in accordance with ACCA Manual J | Loads calculated in accordance with ACCA Manual J
|  |  |  | Or other approved calculation method | Or other approved calculation method
|  | Equipment efficiency |  | ≥Minimum required by federal law for the geographic location where installed | ≥Minimum required by federal law for the geographic location where installed
| Systems serving multiple dwelling units |  |  | Comply with Sections C403 & C404 | Comply with Sections C403 & C404
| Snow melt system controls (Mandatory) |  |  | Snow & ice melting systems | Snow & ice melting systems
|  |  | Automatic controls to turn off system when | Pavement temperature >50°F and | Pavement temperature >50°F and
|  |  |  | No precipitation falling | No precipitation falling
|  |  | Automatic or manual control to allow shutoff when | Outdoor temperature >40°F | Outdoor temperature >40°F
Pools & inground permanently installed spas (Mandatory)
|  |  |  | Accessory to one- and two family dwellings & townhouses ≤3 stories that are available only to household & guests | Accessory to one- and two family dwellings & townhouses ≤3 stories that are available only to household & guests
|  |  | Heaters | Readily accessible on-off switch mounted outside heater to | Readily accessible on-off switch mounted outside heater to
|  |  |  | allow shut off without adjusting thermostat setting | allow shut off without adjusting thermostat setting
|  |  |  | No constant burning pilot on gas-fired units | No constant burning pilot on gas-fired units
|  |  | Time switches or other control method | Turn off & on heaters & pumps according to preset schedule | Turn off & on heaters & pumps according to preset schedule
|  |  | Exceptions: | Required 24-hour operation by public health standard | Required 24-hour operation by public health standard
|  |  |  | Required to operate solar and waste-heat-recovery pool heating systems | Required to operate solar and waste-heat-recovery pool heating systems
|  |  | Covers | Vapor-retardant cover | Vapor-retardant cover
|  |  | Exception: | Deriving >70% heating energy from site-recovered energy over an operating season | Deriving >75% heating energy from site-recovered energy over an operating season
Electrical Power and Lighting Systems (Mandatory)
Lighting equipment (Mandatory)
|  | High-efficacy lamps |  | ≥75% lamps in permanently installed fixtures or
|  |  |  | In ≥75% permanently installed fixtures | In ≥90% permanently installed fixtures
|  | Fuel gas lighting system |  | No continuously burning pilot lights | No continuously burning pilot lights
Simulated Performance Alternate (Performance)
|  |  |  | Allowed | Allowed
Energy Rating Index (ERI)Compliance Alternative
|  | Mandatory requirements |  | Meet all mandatory requirements | Meet all mandatory requirements
|  |  |  | ≥ thermal envelope efficiencies in 2009 IECC | ≥ thermal envelope efficiencies in 2009 IECC
|  |  | Exception: | ≥R-6 duct insulation outside thermal envelope | ≥R-6 duct insulation outside thermal envelope
Energy Rating Index (ERI)
|  |  |  | Consider all energy used | Consider all energy used
|  |  | ERI-based compliance | ≤55 | ≤61
Where on-site renewable energy is included for compliance, building thermal envelope efficiencies ≥ 2015 IECC efficiencies
|  |  | Verification | By approved 3rd party | By approved 3rd party
|  |  | Compliance report | Address / other identification | Address / other identification
|  |  |  | Inspection checklist for component characteristics of rated design | Inspection checklist for component characteristics of rated design
|  |  |  | Inspection checklist show results for reference design and rated design | Inspection checklist show results for reference design and rated design
|  |  |  | Person completing compliance report | Person completing compliance report
|  |  |  | Identify compliance software tool | Identify compliance software tool
Existing Buildings
|  | New and replacement materials |  | Meet new construction requirements | Meet new construction requirements
|  |  |  | except where permitted by this code | except where permitted by this code
Additions
|  | To buildings, building systems or portions thereof |  | Meet new construction requirements | Meet new construction requirements
|  | Where nonconditioned space changed to conditioned space |  | Addition building envelope UA complies | Addition building envelope UA complies
|  |  |  | UA of existing building & addition and any alterations ≤UA for existing building | UA of existing building & addition and any alterations ≤UA for existing building
Heating and cooling systems
|  |  | New ducts | Comply with code | Comply with code
|  |  | Ducts from existing system in unconditioned space | <40 linear feet need not be tested | <40 linear feet need not be tested
Service hot water system
|  |  | Systems part of addition | Comply with code | Comply with code
Lighting
|  |  | New systems part of addition | Comply with code | Comply with code
|  | Existing plus addition compliance (Simulated Performance Alternative) |  | Addition & Alteration comply entirely with Section R405 | Addition & Alteration comply entirely with Section R405
|  |  |  | Annual energy cost (or energy use) of addition & existing building with alterations ≤ cost (use) of existing building | Annual energy cost (or energy use) of addition & existing building with alterations ≤ cost (use) of existing building
Alterations
|  | To buildings, building systems or portions thereof |  | Meet new construction requirements | Meet new construction requirements
|  |  |  | Not increase energy use | Not increase energy use
Building envelope exceptions
|  |  |  | 1) Storm windows over existing fenestration | 1) Storm windows over existing fenestration
|  |  |  | 2) Existing cavities filled with insulation exposed during construction | 2) Existing cavities filled with insulation exposed during construction
|  |  |  | 3) Existing cavities not exposed during construction | 3) Existing cavities not exposed during construction
|  |  |  | 4) Roof recover | 4) Roof recover
|  |  |  | 5) Roofs without insulation in cavity & where sheathing or insulation is exposed during reroofing shall be insulated either above or below sheathing | 5) Roofs without insulation in cavity & where sheathing or insulation is exposed during reroofing shall be insulated either above or below sheathing
|  |  |  | 6) Surface-applied window film on existing single pane fenestration | 6) Surface-applied window film on existing single pane fenestration
|  | Replacement fenestration |  | 0.32 | 0.3
|  | Heating and cooling systems |  | Comply with code | Comply with code
|  |  | Ducts from existing system in unconditioned space | <40 linear feet need not be tested | <40 linear feet need not be tested
|  | Service hot water systems |  | Comply with code | Comply with code
|  | Lighting |  | Comply with code | Comply with code
|  |  | Exception | Replace <50% luminaires in space & not increase lighting power | Replace <50% luminaires in space & not increase lighting power
|  | Change in space conditioning |  | Space bought into full compliance with code | Space bought into full compliance with code
|  |  | Exception | Where simulated performance option is used to comply & | Where simulated performance option is used to comply &
|  |  |  | Proposed annual energy cost ≤110% otherwise allowed annual energy cost | Proposed annual energy cost ≤110% otherwise allowed annual energy cost
Repairs
|  |  | Application (considered repairs) | Glass-only replacement in existing sash & frame | Glass-only replacement in existing sash & frame
|  |  |  | Roof repairs | Roof repairs
|  |  |  | Replace bulb and/or ballast within existing luminaires & not increase installed power | Replace bulb and/or ballast within existing luminaires & not increase installed power
Change of Occupancy or use
|  |  |  | Change resulting in increased energy use must comply | Change resulting in increased energy use must comply
|  |  |  | Change to dwelling unit or portion thereof from another use or occupancy must comply | Change to dwelling unit or portion thereof from another use or occupancy must comply
Appendix RA
Recommended Procedure for Worst-Case Testing of Atmospheric Venting Systems Under R402.4 or R05 Conditions ≤5 ACH50
Recommended to identify problems that weaken draft & restrict combustion air
Where required by code official
Conducted by approved 3rd party
Conducted after creation of all penetrations & prior to final inspection
Appendix |  |  |  | Appendix RB | Appendix RA
Solar-Ready Provisions - Detached One- and Two-Family Dwellings, Multiple Single-Family Dwellings (Townhouses)
|  | Solar-ready zone, definition |  | Section(s) of roof or overhang designated and reserved for future installation of solar photovoltaic or solar thermal | Section(s) of roof or overhang designated and reserved for future installation of solar photovoltaic or solar thermal
|  | General |  | New construction | New construction
|  |  |  | ≥600 sf of roof area oriented between 110° & 270° of true north | ≥600 sf of roof area oriented between 110° & 270° of true north
|  |  | Exceptions: | New residential buildings with permanently installed on-site renewable energy system | New residential buildings with permanently installed on-site renewable energy system
|  |  |  | Solar-ready zone shaded for >70% daylight hours annually | Solar-ready zone shaded for >70% daylight hours annually
|  | Construction documents |  | Indicate solar-ready zone | Indicate solar-ready zone
|  |  | Solar-ready zone area (exclusive of mandatory access or set back areas required by IFC) | ≥300 sf | ≥300 sf
|  |  |  | ≥150 sf on townhouses with floor area ≤2,000 sf per dwelling unit | ≥150 sf on townhouses with floor area ≤2,000 sf per dwelling unit
|  |  |  | ≥5' wide & ≥80 sf | ≥5' wide & ≥80 sf
|  |  | Obstructions | Free from | Free from
|  |  | Roof load documentation | Dead load & live load clearly indicated | Dead load & live load clearly indicated
|  |  | Interconnection pathway | Indicate pathways for routing conduit or plumbing | Indicate pathways for routing conduit or plumbing
|  |  | Electrical service reserved space in main electrical panel | Space for dual pole circuit breaker | Space for dual pole circuit breaker
|  |  |  | Labeled "For Future Solar Electric" | Labeled "For Future Solar Electric"
|  |  |  | Space located at opposite end from feeder input | Space located at opposite end from feeder input
|  |  | Construction document certification | Indicating solar-ready zone & other requirements posted near electrical distribution panel, water heater or other conspicuous location | Indicating solar-ready zone & other requirements posted near electrical distribution panel, water heater or other conspicuous location