## Sheet1
Comparison of Performance Characteristics in ASHRAE/IESNA Standard 90.1
(For Climate Zone 5A)
|  |  |  | 2010 | 2013 | 2016
Scope
|  |  |  | Establish the minimum energy efficiency requirements for design, construction and a plan for operation and maintenance; and for utilization of on-site renewable energy resources. | Minimum energy-efficient requirements for design, construction and a plan for operation and maintenance; and criteria for determining compliance with these requirements | Minimum energy-efficient requirements for design, construction and a plan for operation and maintenance; and criteria for determining compliance with these requirements
|  |  |  | Expanded to new equipment or building systems specifically identified as part of industrial or manufacturing processes. | Applies to commercial buildings, portions of buildings, associated systems and equipment and identified equipment that are part of industrial or manufacturing processes | Applies to commercial buildings, portions of buildings, associated systems and equipment and identified equipment that are part of industrial or manufacturing processes
Building Envelope |  |  |  | Climate Zone 5A | Climate Zone 5A | Climate Zone 5A
Roofs - Non Residential
Insulation Entirely above Deck
|  |  | Assembly Maximum | U-0.048 | U-0.032 | U-0.032
|  |  | Insulation Minimum R-Value | R-20.0 ci | R-30 ci | R-30 ci
Metal Building
|  |  | Assembly Maximum | U-0.055 | U-0.037 | U-0.037
|  |  | Insulation Minimum R-Value | R-13.0 + R-13.0 | R-19 + R-11 LS or R-25 + R-8 LS | R-19 + R-11 LS or R-25 + R-8 LS
Attic and Other
|  |  | Assembly Maximum | U-0.027 | U-0.021 | U-0.021
|  |  | Insulation Minimum R-Value | R-38.0 | R-49 | R-49
Roofs - Residential
Insulation Entirely above Deck
|  |  | Assembly Maximum | U-0.048 | U-0.032 | U-0.032
|  |  | Insulation Minimum R-Value | R-20.0 ci | R-30 ci | R-30 ci
Metal Building
|  |  | Assembly Maximum | U-0.055 | U-0.037 | U-0.037
|  |  | Insulation Minimum R-Value | R-13.0 + R-13.0 | R-19 + R-11 LS or R-25 + R-8 LS | R-19 + R-11 LS or R-25 + R-8 LS
Attic and Other
|  |  | Assembly Maximum | U-0.027 | U-0.021 | U-0.021
|  |  | Insulation Minimum R-Value | R-38.0 | R-49 | R-49
Roofs - Semiheated
Insulation Entirely above Deck
|  |  | Assembly Maximum | U-0.119 | U-0.063 | U-0.063
|  |  | Insulation Minimum R-Value | R-7.6 ci | R-15 ci | R-15 ci
Metal Building
|  |  | Assembly Maximum | U-0.083 | U-0.082 | U-0.082
|  |  | Insulation Minimum R-Value | R-13.0 | R-19 | R-19
Attic and Other
|  |  | Assembly Maximum | U-0.053 | U-0.034 | U-0.034
|  |  | Insulation Minimum R-Value | R-19.0 | R-30 | R-30
Walls, Above Grade - Non Residential
Mass
|  |  | Assembly Maximum | U-0.090 | U-0.090 | U-0.090
|  |  | Insulation Minimum R-Value | R-11.4 ci | R-11.4 ci | R-11.4 ci
Metal Building
|  |  | Assembly Maximum | U-0.069 | U-0.050 | U-0.050
|  |  | Insulation Minimum R-Value | R-13.0 + R-5.6 ci | R-0 + R-19 ci | R-0 + R-19 ci
Steel Framed
|  |  | Assembly Maximum | U-0.064 | U-0.055 | U-0.055
|  |  | Insulation Minimum R-Value | R-13.0 + R-7.5 ci | R-13 + R-10 ci | R-13 + R-10 ci
Wood Framed and Other
|  |  | Assembly Maximum | U-0.064 | U-0.051 | U-0.051
|  |  | Insulation Minimum R-Value | R-13.0 + R-3.8 ci | R-13.0 + R-7.5 ci or R-19 + R-5 ci | R-13.0 + R-7.5 ci or R-19 + R-5 ci
Walls, Above Grade - Residential
Mass
|  |  | Assembly Maximum | U-0.080 | U-0.080 | U-0.080
|  |  | Insulation Minimum R-Value | R-13.3 ci | R-13.3 ci | R-13.3 ci
Metal Building
|  |  | Assembly Maximum | U-0.069 | U-0.050 | U-0.050
|  |  | Insulation Minimum R-Value | R-13.0 + R-5.6 ci | R-0 + R-19 ci | R-0 + R-19 ci
Steel Framed
|  |  | Assembly Maximum | U-0.064 | U-0.055 | U-0.055
|  |  | Insulation Minimum R-Value | R-13.0 + R-7.5 ci | R-13 + R-10 ci | R-13 + R-10 ci
Wood Framed and Other
|  |  | Assembly Maximum | U-0.051 | U-0.051 | U-0.051
|  |  | Insulation Minimum R-Value | R-13.0 + R-7.5 ci | R-13 + R-7.5 ci or R-19 + R-5 ci | R-13 + R-7.5 ci or R-19 + R-5 ci
Walls, Above Grade - Semiheated
Mass
|  |  | Assembly Maximum | U-0.151 | U-0.151 | U-0.151
|  |  | Insulation Minimum R-Value | R-5.7 ci | R-5.7 ci | R-5.7 ci
Metal Building
|  |  | Assembly Maximum | U-0.113 | U-0.094 | U-0.094
|  |  | Insulation Minimum R-Value | R-13.0 | R-0 + R-9.8 ci | R-0 + R-9.8 ci
Steel Framed
|  |  | Assembly Maximum | U-0.124 | U-0.084 | U-0.084
|  |  | Insulation Minimum R-Value | R-13.0 | R-13 + R-3.8 ci | R-13 + R-3.8 ci
Wood Framed and Other
|  |  | Assembly Maximum | U-0.089 | U-0.089 | U-0.089
|  |  | Insulation Minimum R-Value | R-13.0 | R-13 | R-13
Wall, Below Grade - Non Residential
|  |  | Assembly Maximum | C-0.119 | C-0.119 | C-0.119
|  |  | Insulation Minimum R-Value | R-7.5 ci | R-7.5 ci | R-7.5 ci
Wall, Below Grade - Residential
|  |  | Assembly Maximum | C-0.119 | C-0.092 | C-0.092
|  |  | Insulation Minimum R-Value | R-7.5 ci | R-10 ci | R-10 ci
Wall, Below Grade - Semiheated
|  |  | Assembly Maximum | C-1.140 | C-1.140 | C-1.140
|  |  | Insulation Minimum R-Value | NR | NR | NR
Floors - Non Residential
Mass
|  |  | Assembly Maximum | U-0.074 | U-0.057 | U-0.057
|  |  | Insulation Minimum R-Value | R-10.4 ci | R-14.6 ci | R-14.6 ci
Steel Joist
|  |  | Assembly Maximum | U-0.038 | U-0.038 | U-0.038
|  |  | Insulation Minimum R-Value | R-30.0 | R-30 | R-30
Wood Framed and Other
|  |  | Assembly Maximum | U-0.033 | U-0.033 | U-0.033
|  |  | Insulation Minimum R-Value | R-30.0 | R-30 | R-30
Floors - Residential
Mass
|  |  | Assembly Maximum | U-0.064 | U-0.051 | U-0.051
|  |  | Insulation Minimum R-Value | R-12.5 ci | R-16.7 ci | R-16.7 ci
Steel Joist
|  |  | Assembly Maximum | U-0.038 | U-0.038 | U-0.038
|  |  | Insulation Minimum R-Value | R-30.0 | R-30 | R-30
Wood Framed and Other
|  |  | Assembly Maximum | U-0.033 | U-0.033 | U-0.033
|  |  | Insulation Minimum R-Value | R-30.0 | R-30 | R-30
Floors - Semiheated
Mass
|  |  | Assembly Maximum | U-0.137 | U-0.107 | U-0.107
|  |  | Insulation Minimum R-Value | R-4.2 ci | R-6.3 ci | R-6.3 ci
Steel Joist
|  |  | Assembly Maximum | U-0.052 | U-0.052 | U-0.052
|  |  | Insulation Minimum R-Value | R-19.0 | R-19 | R-19
Wood Framed and Other
|  |  | Assembly Maximum | U-0.051 | U-0.051 | U-0.051
|  |  | Insulation Minimum R-Value | R-19.0 | R-19 | R-19
Slab-On-Grade Floors - Non Residential
Unheated
|  |  | Assembly Maximum | F-0.730 | F-0.520 | F-0.520
|  |  | Insulation Minimum R-Value | NR | R-15 for 24" | R-15 for 24"
Heated
|  |  | Assembly Maximum | F-0.860 | F-0.688 | F-0.688
|  |  | Insulation Minimum R-Value | R-15 for 24 in. | R-20 for 48" | R-20 for 48"
Slab-On-Grade Floors - Residential
Unheated
|  |  | Assembly Maximum | F-0.540 | F-0.510 | F-0.510
|  |  | Insulation Minimum R-Value | R-10 for 24 in. | R-20 for 24" | R-20 for 24"
Heated
|  |  | Assembly Maximum | F-0.860 | F-0.688 | F-0.688
|  |  | Insulation Minimum R-Value | R-15 for 24 in. | R-20 for 48" | R-20 for 48"
Slab-On-Grade Floors - Semiheated
Unheated
|  |  | Assembly Maximum | F-0.730 | F-0.730 | F-0.730
|  |  | Insulation Minimum R-Value | NR | NR | NR
Heated
|  |  | Assembly Maximum | F-1.020 | F-0.900 | F-0.900
|  |  | Insulation Minimum R-Value | R-7.5 for 12 in. | R-10 for 24" | R-10 for 24"
Opaque Doors - Non Residential
Swinging
|  |  | Assembly Maximum | U-0.700 | U-0.500 | U-0.370
Non-Swinging
|  |  | Assembly Maximum | U-0.500 | U-0.500 | U-0.310
Opaque Doors - Residential
Swinging
|  |  | Assembly Maximum | U-0.500 | U-0.500 | U-0.370
Non-Swinging
|  |  | Assembly Maximum | U-0.500 | U-0.500 | U-0.310
Opaque Doors - Semiheated
Swinging
|  |  | Assembly Maximum | U-0.700 | U-0.700 | U-0.370
Non-Swinging
|  |  | Assembly Maximum | U-1.450 | U-1.450 | U-0.310
| Skylight Curbs |  | Insulation | R-5 | R-5 | R-5
Fenestration - Non Residential
Vertical Glazing, 0-40% of Wall
|  |  | Nonmetal Framing (all) | U-0.35 | U-0.32 | U-0.31
|  |  | Metal Framing, fixed | U-0.45 | U-0.42 | U-0.38
|  |  | Metal Framing, operable |  | U-0.50 | U-0.46
|  |  | Metal Framing, entrance door | U-0.80 | U-0.77 | U-0.68
|  |  | Metal Framing (all Other) | U-0.55
|  |  | Solar Heat Gain Coefficient, all | SHGC-0.40 | SHGC-0.40 | SHGC-0.38
|  |  | VT/SHGC, all |  | 1.1 | 1.1
Skylight, all types, 0-3% of Roof
|  |  | Assembly Maximum |  | U-0.50 | U-0.50
|  |  | Assembly Maximum |  | SHGC-0.40 | SHGC-0.40
Skylight with Curb, Glass, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.17
|  |  | Assembly Maximum | SHGC-0.49
Skylight with Curb, Glass, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.17
|  |  | Assembly Maximum | SHGC-0.39
Skylight with Curb, Plastic, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.10
|  |  | Assembly Maximum | SHGC-0.77
Skylight with Curb, Plastic, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.10
|  |  | Assembly Maximum | SHGC-0.62
Skylight without Curb, All, 0-2.0% of Roof
|  |  | Assembly Maximum | U-0.69
|  |  | Assembly Maximum | SHGC-0.49
Skylight without Curb, All, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-0.69
|  |  | Assembly Maximum | SHGC-0.39
Fenestration - Residential
Vertical Glazing, 0-40% of Wall
|  |  | Nonmetal Framing (all) | U-0.35 | U-0.32 | U-0.31
|  |  | Metal Framing, fixed | U-0.45 | U-0.42 | U-0.38
|  |  | Metal Framing, operable |  | U-0.50 | U-0.46
|  |  | Metal Framing, entrance door) | U-0.80 | U-0.68 | U-0.68
|  |  | Metal Framing (all Other) | U-0.55
|  |  | Solar Heat Gain Coefficient, all | SHGC-0.40 | SHGC-0.40 | SHGC-0.38
|  |  | VT/SHGC, all |  | 1.1 | 1.1
Skylight, all types, 0-3% of Roof
|  |  | Assembly Maximum |  | U-0.50 | U-0.50
|  |  | Assembly Maximum |  | SHGC-0.40 | SHGC-0.40
Skylight with Curb, Glass, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.17
|  |  | Assembly Maximum | SHGC-0.49
Skylight with Curb, Glass, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.17
|  |  | Assembly Maximum | SHGC-0.39
Skylight with Curb, Plastic, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.10
|  |  | Assembly Maximum | SHGC-0.77
Skylight with Curb, Plastic, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.10
|  |  | Assembly Maximum | SHGC-0.62
Skylight without Curb, All, 0-2.0% of Roof
|  |  | Assembly Maximum | U-0.69
|  |  | Assembly Maximum | SHGC-0.49
Skylight without Curb, All, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-0.69
|  |  | Assembly Maximum | SHGC-0.39
Fenestration - Semiheated
Vertical Glazing, 0-40% of Wall
|  |  | Nonmetal Framing (all) | U-1.20 | U-0.45 | U-0.45
|  |  | Metal Framing, fixed | U-1.20 | U-0.62 | U-0.62
|  |  | Metal Framing, operable |  | U-0.70 | U-0.70
|  |  | Metal Framing, entrance door) | U-1.20 | U-0.77 | U-0.77
|  |  | Metal Framing (all Other) | U-1.20
|  |  | Solar Heat Gain Coefficient, all | SHGC-NR | NR | NR
|  |  | VT/SHGC, all |  | NR | NR
Skylight, all types, 0-3% of Roof
|  |  | Assembly Maximum |  | U-0.98 | U-0.98
|  |  | Assembly Maximum |  | SHGC - NR | SHGC-0.40
Skylight with Curb, Glass, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.98
|  |  | Assembly Maximum | SHGC-NR
Skylight with Curb, Glass, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.98
|  |  | Assembly Maximum | SHGC-NR
Skylight with Curb, Plastic, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.90
|  |  | Assembly Maximum | SHGC-NR
Skylight with Curb, Plastic, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.90
|  |  | Assembly Maximum | SHGC-NR
Skylight without Curb, All, 0-2.0% of Roof
|  |  | Assembly Maximum | U-1.36
|  |  | Assembly Maximum | SHGC-NR
Skylight without Curb, All, 2.1-5.0% of Roof
|  |  | Assembly Maximum | U-1.36
|  |  | Assembly Maximum | SHGC-NR
Fenestration
|  | Allowed increase to vertical fenestration area |  |  | ≥40% When vertical fenestration on street side of street-level story only, provided: | ≥40% When vertical fenestration on street side of street-level story only, provided:
[5 empty] | a) Street side of street-level story ≤20 ft in height | a) Street side of street-level story ≤20 ft in height
[5 empty] | b) Fenestration has continuous overhang with weighted average PF >0.5 | b) Fenestration has continuous overhang with weighted average PF >0.5
[5 empty] | c) Fenestration area for street side of street-level story <75% gross wall area for street side of street-level story | c) Fenestration area for street side of street-level story <75% gross wall area for street side of street-level story
|  | Allowed increase to skylight fenestration area |  |  | ≤6% of gross roof area, provided | ≤6% of gross roof area, provided
[5 empty] | a) Glazing matterial or diffuser has haze value >90% | a) Glazing matterial or diffuser has haze value >90%
[5 empty] | b) Skylight VT >0.40 | b) Skylight VT >0.40
[5 empty] | c) Multilevel photocontrols of all general lighting in daylight area under skylight | c) Multilevel photocontrols of all general lighting in daylight area under skylight
Fenestration Orientation
|  |  |  | As≥Aw and As≥AE: Exceptions for Existing Shading and Alterations/Additions That Do Not Increase Vertical Fenestration Area | Comply with either: | Comply with either:
[5 empty] | AW ≤ (AT)/4 and | AW ≤ (AT)/4 and
[5 empty] | AE ≤ (AT)/4 | AE ≤ (AT)/4
[5 empty] | or | or
[5 empty] | AW x SHGCW ≤ (AT x SHGCC)/4 and | AW x SHGCW ≤ (AT x SHGCC)/5 and
[5 empty] | AE x SHGCE ≤ (AT x SHGCC)/4 | AE x SHGCE ≤ (AT x SHGCC)/5
Required Skylights
|  |  | Required locations | Buildings ≤4 Stories | All Enclosed Spaces | All Enclosed Spaces
|  |  |  | Enclosed Space ≥5,000 sq ft | ≥2,500 sq ft | ≥2,500 sq ft
|  |  |  | Under Roof with Ceiling Heights >15 ft | Under roof with ceiling heights >15 ft | Under roof with ceiling heights >15 ft
|  |  | In defined space type | Office, Lobby, Atrium, Concourse, Corridor, Nonrefrigerated warehouse or storage, Gymnasium/Exercise center, Playing area, Gymnasium seating area, Convention center, Automotive service, Manufacturing, Retail, Distribution/sorting area, Transportation, or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage (including nonrefrigerated warehouse), Gymnasium, Fitness/exercise area, Playing area, Gymnasium seating area, Convention exhibit/event space, Courtroom, Automotive service, Fire station engine room, Manufacturing corridor/transition and bay areas, Retail, Library reading and stack areas, Distribution/sorting area, Transportation baggage and seating areas, or Workshop | Office, Lobby, Atrium, Concourse, Corridor, Storage (including nonrefrigerated warehouse), Gymnasium, Fitness/exercise area, Playing area, Gymnasium seating area, Convention exhibit/event space, Courtroom, Automotive service, Fire station engine room, Manufacturing corridor/transition and bay areas, Retail, Library reading and stack areas, Distribution/sorting area, Transportation baggage and seating areas, or Workshop
Applies To Unconditioned Spaces
|  |  | Minimum Required Skylight Fenestration Area | Daylight Area Under Skylights ≥50% Floor Area and Either: | Total daylight zone under skylight ≥50% floor area | Total daylight zone under skylight ≥50% floor area
|  |  |  | Minimum Skylight Area to Daylight Area Under Skylights of 3% with Skylight VLT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or | Minimum skylight area to daylight zone under skylight ≥3% with skylight VT ≥0.40 or
|  |  |  | Provide Minimum Skylight Effective Aperature of ≥1% | Skylight effective aperture ≥1% | Skylight effective aperture ≥1%
|  |  |  | Haze Value >90% | Haze value >90% | Haze value >90%
|  |  | Skylight SHGC Exemption | LPD <0.5 w/sf
|  |  |  | ≥50% Roof Areas Blocked By Existing Buildings or Natural Objects for >1,500 Daytime Hours Between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm | ≥50% roof areas blocked by existing buildings or natural objects for >1,500 daytime hours per year between 8 am & 4 pm
|  |  |  | Daylight Area Under Roof Monitors >50% Enclosed Space Floor Area | Daylight area under roof monitors >50% enclosed space floor area | Daylight area under roof monitors >50% enclosed space floor area
[5 empty] | Enclosed spaces where total area minus primary & secondary sidelighted area(s) <2,500 sf and where lighting is controlled to sidelighting requirements | Enclosed spaces where total area minus primary & secondary sidelighted area(s) <2,500 sf and where lighting is controlled to sidelighting requirements
[5 empty] | Enclosed space where 90% skylight area shaded on June 21 @ noon by permanent architectural features of building | Enclosed space where 90% skylight area shaded on June 21 @ noon by permanent architectural features of building
| Compliance Path: Prescriptive Building Envelope |  |  | Vertical Fenestration ≤40% Gross Wall Area: Skylight Fenestration ≤5% Gross Roof Area | Vertical Fenestration ≤40% Gross Wall Area: Skylight Fenestration ≤3% Gross Roof Area | Vertical Fenestration ≤40% Gross Wall Area: Skylight Fenestration ≤3% Gross Roof Area
| Compliance Path: Building Envelope Trade-Off |  |  | Allowed | Allowed | Allowed
| Projection Factor Vertical Fenestration SHGC Adjustment |  |  | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF | Table for SHGC multipliers for permanent projections by orientation for 0.1 increments in PF
| Dynamic Glazing |  |  | Minimum SHGC Used to Demonstrate Compliance, Can Not Be Used In Averaging | Minimum SHGC used to demonstrate compliance, cannot be used in averaging | Minimum SHGC used to demonstrate compliance, cannot be used in averaging
Insulation Instlation
|  |  | Eave Vent Baffles |  |  | Required with eave vents
|  |  | Substantial contact |  | In substantial contact with inside surface in accordance with manufacturers' recommendations for framing system used | In substantial contact with inside surface in accordance with manufacturers' recommendations for framing system used
|  |  | Recessed HVAC equipment in thermal envelope |  | Not recessed in manner as to affect insulation thickness | Not recessed in manner as to affect insulation thickness
|  |  | Recessed lighting In thermal envelope |  | Not recessed in manner as to affect insulation thickness | Not recessed in manner as to affect insulation thickness
[5 empty] | Comply with envelope air leakage requirements | Comply with envelope air leakage requirements
|  |  | Extent of insulation |  |  | Over full component area
|  |  | Rigid Insulation | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers | Joints To Be Staggered on Multiple Layers
Air Leakage
|  |  | Loading Dock Weatherseals | Yes | Yes | Yes
|  |  | Building Entrance Vestibules | Building Entrances ≥1000 sf To Space ≥3000 sf Without Revolving Door | Building entrance from space ≥1,000 sf without revolving door | Building entrance from space ≥1,000 sf without revolving door
[5 empty] | Doors opening directly from space ≥3,000 sf and is not separated from building entrance | Doors opening directly from space ≥3,000 sf and is not separated from building entrance
[5 empty] | Vestibule floor area ≤50 sf or 2% of gross conditioned floor area of that level | Vestibule floor area ≤50 sf or 2% of gross conditioned floor area of that level
[5 empty] | Exterior envelope of conditioned vestibule meet requirements for conditioned space | Exterior envelope of conditioned vestibule meet requirements for conditioned space
[5 empty] | Interior & exterior envelope of unconditioned vestibule meet requirements for semiheated space | Interior & exterior envelope of unconditioned vestibule meet requirements for semiheated space
Air Leakage for Fenestration & Doors
Maximum Infiltration Rate for Fenestration Assemblies
|  |  | All other products |  |  | 0.20 cfm/sf
|  |  | Windows | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Sliding Doors | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Swinging Doors | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Skylights - with Condensation Weepage Openings | 0.30 cfm/sf | 0.30 cfm/sf | 0.30 cfm/sf
|  |  | Skylights - All Other | 0.20 cfm/sf | 0.20 cfm/sf
|  |  | Curtain Wall | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf
|  |  | Storefront Glazing | 0.06 cfm/sf | 0.06 cfm/sf | 0.06 cfm/sf
|  |  | Commercial Glazed Swinging Entrance Doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf
|  |  | Glazed power-operated sliding entrance doors, glazed power-operated folding entrance doors |  |  | 1.00 cfm/sf
|  |  | Revolving Doors | 1.00 cfm/sf | 1.00 cfm/sf | 1.00 cfm/sf
|  |  | Garage Doors | 0.40 cfm/sf | 0.40 cfm/sf | 0.40 cfm/sf
|  |  | Rolling doors |  | 1.3 cfm/sf
|  |  | High-speed doors |  | 1.3 cfm/sf | 1.3 cfm/sf
|  | Continuous Air Barriers |  | Extend Over All Surfaces | Continuous throughout thermal envelope | Required except for semiheated spaces
|  |  |  | Constructed with Defined Materials & Assmblies or Tested Air Leakage Rate ≤0.40 cfm/sf | Continuous for all assemblies
All joints and seams sealed including transitions in places and changes in materials
All penetrations sealed
Ability to resist positive and negative pressure
Materials with air permeability ≤0.004 cfm/sf
|  |  | Design |  |  | Continuous air barrier clearly identified on construction documents
Joints, interconnections and penestrations shall be detailed
Extend over all surfaces
Designed to resist positive & negative pressures
|  |  | Air Barrier Compliance Options |  |  | Compliance with (a), (b) or (c )
[5 empty] | Materials with air permeability ≤0.004 cfm/sf | (a) Whole-building presurized testing with leakage rate ≤0.40 cfm/sf at 0.3" wc
[5 empty] | Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf | Exception to (a)
1: Less than whole building for buildings >50,000 sf
2: When diagnostic evaluation is conducted and any leaks sealed if sealing can be done without destruction of existing building components where leakage rate >0.40 but <0.60 cfm/sf
(b) Material with air permeability ≤0.004 cfm/sf
(c )Assemblies of materials and components with average air leakage rate ≤0.04 cfm/sf
|  |  | Air Barrier Installation | Wrap, Seal, Caulk, Gasket or Tape Joints, Junctions, Penetrations, Building Assemblies, Seams, Connections & Changes in Air Barrier Materials | Wrap, Seal, Caulk, Gasket or Tape Joints, Junctions, Penetrations, Building Assemblies, Seams, Connections & Changes in Air Barrier Materials | Wrap, Seal, Caulk, Gasket or Tape Joints, Junctions, Penetrations, Building Assemblies, Seams, Connections & Changes in Air Barrier Materials
Including building assemblies used as ducts or plenums
|  | Air Leakage Verification |  |  |  | Air barrier design review
Periodic field inspection of continuous air barrier
Whole-building air leakage verification program
Heating, Ventilating and Air Conditioning
| Simplified Approach |  |  | ≤2 Stories and ≤25,000 sf with Compliant HVAC Systems | ≤2 stories and ≤25,000 sf with compliant single zone HVAC system | ≤2 stories and ≤25,000 sf with compliant single zone HVAC system
[5 empty] | Has defined criteria and requirements | Has defined criteria and requirements
| Equipment and System Sizing |  |  | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations | Use Standard 183 for heating and cooling system design load calculations
|  |  |  | Calculate pressure drop through each device and pipe segment in critical circuit at design conditions | Calculate pressure drop through each device and pipe segment in critical circuit at design conditions | Calculate pressure drop through each device and pipe segment in critical circuit at design conditions
Mechanical Equipment Efficiency
Air Conditioners, Air Cooled
|  | <65,000 Btu/h, Split Systems |  | 13.0 SEER | 13.0 SEER | 13.0 SEER
|  | <65,000 Btu/h, Single Package |  | 13.0 SEER | 14.0 SEER | 14.0 SEER
|  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 11.2 EER 11.4 IEER | 11.2 EER 12.9 IEER | 11.2 EER 12.9 IEER
|  | ≥65,000 & <135,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 11.0 EER 11.2 IEER | 11.0 EER 12.7 IEER | 11.0 EER 12.7 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 11.0 EER 11.2 IEER | 11.0 EER 12.4 IEER | 11.0 EER 12.4 IEER
|  | ≥135,000 & <240,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 10.8 EER 11.0 IEER | 10.8 EER 12.2 IEER | 10.8 EER 12.2 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 10.0 EER 10.1 IEER | 10.0 EER 11.6 IEER | 10.0 EER 11.6 IEER
|  | ≥240,000 & <760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 9.8 EER 9.9 IEER | 9.8 EER 11.4 IEER | 9.8 EER 11.4 IEER
|  | ≥760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 9.7 EER 9.8 IEER | 9.7 EER 11.2 IEER | 9.7 EER 11.2 IEER
|  | ≥760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 9.5 EER 9.6 IEER | 9.5 EER 11.0 IEER | 9.5 EER 11.0 IEER
|  | ≤30,000 Btu/h Through-the-Wall, Split System |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | ≤30,000 Btu/h Through-the-Wall, Single Package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | <65,000 Btu/h Small-Duct High Velocity, Split System |  |  | 11.0 SEER | 11.0 SEER
Air Conditioner, Water Cooled
|  | <65,000 Btu/h, Split Systems and Single Package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.1 EER 12.3 IEER | 12.1 EER 13.9 IEER | 12.1 EER 13.9 IEER
|  | ≥65,000 & <135,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 11.9 EER 12.1 IEER | 11.9 EER 13.7 IEER | 11.9 EER 13.7 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.5 EER 12.5 IEER | 12.5 EER 13.9 IEER | 12.5 EER 13.9 IEER
|  | ≥135,000 & <240,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 12.3 EER 12.5 IEER | 12.3 EER 13.7 IEER | 12.3 EER 13.7 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.4 EER 12.6 IEER | 12.4 EER 13.6 IEER | 12.4 EER 13.6 IEER
|  | ≥240,000 & < 760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 12.2 EER 12.4 IEER | 12.2 EER 13.4 IEER | 12.2 EER 13.4 IEER
|  | ≥760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.2 EER 12.4 IEER | 12.2 EER 13.5 IEER | 12.2 EER 13.5 IEER
|  | ≥760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 12.0 EER 12.2 IEER | 12.0 EER 13.3 IEER | 12.0 EER 13.3 IEER
Air Conditioner, Evaporatively Cooled
|  | <65,000 Btu/h, Split Systems and Single Package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER | 12.1 EER 12.3 IEER
|  | ≥65,000 & <135,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER | 12.0 EER 12.2 IEER
|  | ≥135,000 & <240,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER | 11.8 EER 12.0 IEER
|  | ≥240,000 & <760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER | 11.9 EER 12.1 IEER
|  | ≥240,000 & < 760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 12.2 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER | 11.7 EER 11.9 IEER
|  | ≥760,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER | 11.5 EER 11.7 IEER
Condensing Units, Air Cooled
|  |  | ≥135,000 Btu/h | 10.5 EER 11.8 IEER | 10.5 EER 11.8 IEER | 10.5 EER 11.8 IEER
Condensing Units, Water Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IEER | 13.5 EER 14.0 IEER | 13.5 EER 14.0 IEER
Condensing Units, Evaporatively Cooled
|  |  | ≥135,000 Btu/h | 13.5 EER 14.0 IEER | 13.5 EER 14.0 IEER | 13.5 EER 14.0 IEER
Heat Pumps, Electrically Operated, Air Cooled (Cooling Mode)
|  | <65,000 Btu/h, Split Systems |  | 13.0 SEER | 14.0 SEER | 14.0 SEER
|  | <65,000 Btu/h, Single Package |  | 13.0 SEER | 14.0 SEER | 14.0 SEER
|  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 11.0 EER 11.2 IEER | 11.0 EER 12.2 IEER | 11.0 EER 12.2 IEER
|  | ≥65,000 & <135,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 10.8 EER 11.0 IEER | 10.8 EER 12.0 IEER | 10.8 EER 12.0 IEER
|  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 10.6 EER 10.7 IEER | 10.6 EER 11.6 IEER | 10.6 EER 11.6 IEER
|  | ≥135,000 & <240,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 10.4 EER 10.5 IEER | 10.4 EER 11.4 IEER | 10.4 EER 11.4 IEER
|  | ≥240,000 Btu/h, Electric Resistance (or None) Heating Section, Split System and Single Package |  | 9.5 EER 9.6 IEER | 9.5 EER 10.6 IEER | 9.5 EER 10.6 IEER
|  | ≥240,000 Btu/h, All Other Heating Section, Split System and Single Package |  | 9.3 EER 9.4 IEER | 9.3 EER 9.4 IEER | 9.3 EER 9.4 IEER
|  | ≤30,000 Btu/h Through-the-Wall, Split System |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | ≤30,000 Btu/h Through-the-Wall, Single Package |  | 12.0 SEER | 12.0 SEER | 12.0 SEER
|  | <65,000 Btu/h Small-Duct High Velocity, Split System |  |  | 11.0 SEER | 11.0 SEER
| Heat Pumps, Electrically Operated, Water to Air, Water loop, 86ºF Entering Water (Cooling Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  |  | <17,000 Btu/h | 11.2 EER | 12.2 EER | 12.2 EER
|  |  | ≥17,000 & <65,000 Btu/h | 12.0 EER | 13.0 EER | 13.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 12.0 EER | 13.0 EER | 13.0 EER
| Heat Pumps, Electrically Operated, Water to Water, Water loop, 86ºF Entering Water (Cooling Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  |  | <135,000 Btu/h | 10.6 EER | 10.6 EER | 10.6 EER
| Heat Pumps, Electrically Operated, Water to Air, Groundwater Source, 59ºF Entering Water (Cooling Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  |  | <135,000 Btu/h | 16.2 EER | 18.0 EER | 18.0 EER
| Heat Pumps, Electrically Operated, Water to Water, Groundwater Source, 59ºF Entering Water (Cooling Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  |  | <135,000 Btu/h | 16.3 EER | 16.3 EER | 16.3 EER
| Heat Pumps, Electrically Operated, Brine to Air, Ground Loop, 77ºF Entering Water (Cooling Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  |  | <135,000 Btu/h | 13.4 EER | 14.1 EER | 14.1 EER
| Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 77ºF Entering Water (Cooling Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  |  | <135,000 Btu/h | 12.1 EER | 12.1 | 12.1
Heat Pumps, Electrically Operated, Air Cooled (Heating Mode)
|  | <65,000 Btu/h (Cooling Capacity), Split Systems |  | 7.7 HSPF | 8.2 HSPF | 8.2 HSPF
|  | <65,000 Btu/h (Cooling Capacity), Single Package |  | 7.7 HSPF | 8.0 HSPF | 8.0 HSPF
|  | ≥65,000 & <135,000 Btu/h (Cooling Capacity), 47ºF db/43ºF wb Outdoor Air |  | 3.3 COP | 3.3 COP | 3.3 COP
|  | ≥65,000 & <135,000 Btu/h (Cooling Capacity), 17ºF db/15ºF wb Outdoor Air |  | 2.25 COP | 2.25 COP | 2.25 COP
|  | ≥135,000 Btu/h (Cooling Capacity), 47ºF db/43ºF wb Outdoor Air |  | 3.2 COP | 3.2 COP | 3.2 COP
|  | ≥135,000 Btu/h (Cooling Capacity), 17ºF db/15ºF wb Outdoor Air |  | 2.05 COP | 2.05 COP | 2.05 COP
|  | ≤30,000 Btu/h Through-the-Wall, Split System |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF
|  | ≤30,000 Btu/h Through-the-Wall, Single Package |  | 7.4 HSPF | 7.4 HSPF | 7.4 HSPF
|  | <65,000 Btu/h Small-Duct High Velocity, Split System |  |  | 6.8 HSPF | 6.8 HSPF
| Heat Pumps, Electrically Operated, Water to Air, Water Loop, 68ºF Entering Water (Heating Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  | <135,000 Btu/h (Cooling Capacity) |  | 4.2 COP | 4.3 COP | 4.3 COP
| Heat Pumps, Electrically Operated, Water to Air, Groundwater Source, 50ºF Entering Water (Heating Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  | <135,000 Btu/h (Cooling Capacity) |  | 3.6 COP | 3.7 COP | 3.7 COP
| Heat Pumps, Electrically Operated, Brine to Air, Ground Loop, 32ºF Entering Water (Heating Mode) |  |  | ISO-13256-1 | ISO-13256-1 | ISO-13256-1
|  | <135,000 Btu/h (Cooling Capacity) |  | 3.1 COP | 3.2 COP | 3.2 COP
| Heat Pumps, Electrically Operated, Water to Water, Water Loop, 68ºF Entering Water (Heating Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  | <135,000 Btu/h (Cooling Capacity) |  | 3.7 COP | 3.7 COP | 3.7 COP
| Heat Pumps, Electrically Operated, Water to Water Groundwater Source, 50ºF Entering Water (Heating Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  | <135,000 Btu/h (Cooling Capcaity) |  | 3.1 COP | 3.1 COP | 3.1 COP
| Heat Pumps, Electrically Operated, Brine to Water, Ground Loop, 32ºF Entering Fluid (Heating Mode) |  |  | ISO-13256-2 | ISO-13256-2 | ISO-13256-2
|  | <135,000 Btu/h (Cooling Capcaity) |  | 2.5 COP | 2.5 COP | 2.5 COP
Water Chiller, Air Cooled, with Condenser, Electrically Operated
|  |  | <150 tons: Path A | ≥9.562 EER ≥12.500 IPLV | ≥10.100 EER ≥13.700 IPLV | ≥10.100 EER ≥13.700 IPLV.IP
|  |  | <150 tons: Path B | NA | ≥9.700 EER ≥15.800 IPLV | ≥9.700 EER ≥15.800 IPLV.IP
|  |  | ≥150 tons: Path A | ≥9.562 EER ≥12.750 IPLV | ≥10.100 EER ≥14.000 IPLV | ≥10.100 EER ≥14.000 IPLV.IP
|  |  | ≥150 tons: Path B | NA | ≥9.700 EER ≥16.100 IPLV | ≥9.700 EER ≥16.100 IPLV.IP
Water Chiller, Air Cooled, without Condenser, Electrically Operated
|  |  | All Capacities | Must Be Rated with Matching Condenser and Comply with Air-Cooled Chiller Efficiency Requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements | Must be rated with matching condenser and comply with air-cooled chiller efficiency requirements
Water Chiller, Water Cooled, Electrically Operated, Positive Displacement (Reciprocating)
|  |  | All Capacities | Must Comply with Water Cooled Positive Displacement Efficiency Requirements
Water Chiller, Water Cooled, Electrically Operated, Positive Displacement
|  |  | <75 tons: Path A | ≤0.780 kW/ton Full & ≤0.630 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV | ≤0.750kW/ton FL & ≤0.600 kW/ton IPLV.IP
|  |  | <75 tons: Path B | ≤0.800 kW/ton Full & ≤0.600 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.780 kW/ton FL & ≤0.500 kW/ton IPLV.IP
|  |  | ≥75 & <150 tons: Path A | ≤0.775 kW/ton Full & ≤0.615 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV | ≤0.720 kW/ton FL & ≤0.560 kW/ton IPLV.IP
|  |  | ≥75 & <150 tons: Path B | ≤0.790 kW/ton Full & ≤0.586 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV | ≤0.750 kW/ton FL & ≤0.490 kW/ton IPLV.IP
|  |  | ≥150 & <300 tons: Path A | ≤0.680 kW/ton Full & ≤0.580 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV | ≤0.660 kW/ton FL & ≤0.540 kW/ton IPLV.IP
|  |  | ≥150 & <300 tons: Path B | ≤0.718 kW/ton Full & ≤0.540 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.680 kW/ton FL & ≤0.440 kW/ton IPLV.IP
|  |  | ≥300 & <600 tons: Path A | ≤0.620 kW/ton Full & ≤0.540 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.520 kW/ton IPLV.IP
|  |  | ≥300 & <600 tons: Path B | ≤0.639 kW/ton Full & ≤0.490 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV | ≤0.625 kW/ton FL & ≤0.410 kW/ton IPLV.IP
|  |  | ≥600 tons Path A | ≤0.620 kW/ton Full & ≤0.540 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV.IP
|  |  | ≥600 tons Path B | ≤0.639 kW/ton Full & ≤0.490 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV.IP
Water Chiller, Water Cooled, Electrically Operated, Centrifugal
|  |  | <150 tons: Path A | ≤0.634 kW/ton Full & ≤0.596 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV.IP
|  |  | <150 tons: Path B | ≤0.639 kW/ton Full & ≤0.450 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV | ≤0.695 kW/ton FL & ≤0.440 kW/ton IPLV.IP
|  |  | ≥150 & <300 tons: Path A | ≤0.634 kW/ton Full & ≤0.596 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV | ≤0.610 kW/ton FL & ≤0.550 kW/ton IPLV.IP
|  |  | ≥150 & <300 tons: Path B | ≤0.639 kW/ton Full & ≤0.450 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV | ≤0.635 kW/ton FL & ≤0.400 kW/ton IPLV.IP
|  |  | ≥300 & <400 tons: Path A | ≤0.576 kW/ton Full & ≤0.549 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.520 kW/ton IPLV.IP
|  |  | ≥300 & <400 tons: Path B | ≤0.600 kW/ton Full & ≤0.400 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV | ≤0.595 kW/ton FL & ≤0.390 kW/ton IPLV.IP
|  |  | ≥400 & <600 tons: Path A | ≤0.576 kW/ton Full & ≤0.549 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV.IP
|  |  | ≥400 & <600 tons: Path B | ≤0.600 kW/ton Full & ≤0.400 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV.IP
|  |  | ≥600 tons: Path A | ≤0.570 kW/ton Full & ≤0.539 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV | ≤0.560 kW/ton FL & ≤0.500 kW/ton IPLV.IP
|  |  | ≥600 tons: Path B | ≤0.590 kW/ton Full & ≤0.400 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV | ≤0.585 kW/ton FL & ≤0.380 kW/ton IPLV.IP
Water Chiller, Air Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.600 COP Full & NR IPLV | ≥0.600 COP FL | ≥0.600 COP FL
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Water Cooled Absorption Single Effect
|  |  | All Capacities: Path A | ≥0.700 COP Full & NR IPLV | ≥0.700 COP FL | ≥0.700 COP FL
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Absorption Double Effect, Indirect-Fired
|  |  | All Capacities: Path A | ≥1.000 COP Full & ≥1.050 IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV | ≥1.000 COP FL & ≥1.050 COP IPLV.IP
|  |  | All Capacities: Path B | NA | NA | NA
Water Chiller, Absorption Double Effect, Direct-Fired
|  |  | All Capacities: Path A | ≥1.000 COP Full & ≥1.000 IPLV | ≥1.000 COP FL & ≥1.000 IPLV | ≥1.000 COP FL & ≥1.000 IPLV.IP
|  |  | All Capacities: Path B | NA | NA | NA
| Electrically Operated Package Terminal Air Conditioners & Heat Pumps |  |  |  |  | as of 1/1/2015
|  | PTAC (Cooling Mode) Standard Size |  | 13.8 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER
|  | PTAC (Cooling Mode) Nonstandard Size |  | 10.9 - (0.213 x Cap/1000) EER | 10.9 - (0.213 x Cap/1000) EER | 10.9 - (0.213 x Cap/1000) EER
|  | PTHP (Cooling Mode) Standard Size |  | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER | 14.0 - (0.300 x Cap/1000) EER
|  | PTHP (Cooling Mode) Nonstandard Size |  | 10.8 - (0.213 x Cap/1000) EER | 10.8 - (0.213 x Cap/1000) EER | 10.8 - (0.213 x Cap/1000) EER
|  | PTHP (Heating Mode) Standard Size |  | 3.7 - (0.052 x Cap/1000) COP | 3.7 - (0.052 x Cap/1000) COP | 3.7 - (0.052 x Cap/1000) COP
|  | PTHP (Heating Mode) Nonstandard Size |  | 2.9 - (0.026 x Cap/1000) COP | 2.9 - (0.026 x Cap/1000) COP | 2.9 - (0.026 x Cap/1000) COP
SPVAC
|  |  | <65,000 Btu/h | 9.0 EER | 10.0 EER | 10.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 10.0 EER | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 10.0 EER | 10.0 EER
SPVHP (Cooling Mode)
|  |  | <65,000 Btu/h | 9.0 EER | 10.0 EER | 10.0 EER
|  |  | ≥65,000 & <135,000 Btu/h | 8.9 EER | 10.0 EER | 10.0 EER
|  |  | ≥135,000 & <240,000 Btu/h | 8.6 EER | 10.0 EER | 10.0 EER
SPVHP (Heating Mode)
|  |  | <65,000 Btu/h | 3.0 COP | 3.0 COP | 3.0 COP
|  |  | ≥65,000 & <135,000 Btu/h | 3.0 COP | 3.0 COP | 3.0 COP
|  |  | ≥135,000 & <240,000 Btu/h | 2.9 COP | 3.0 COP | 3.0 COP
SPVAC (cooling mode), nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  | 9.2 EER | 9.2 EER
|  |  | >30,000 and ≤36,000 Btu/h |  | 9.0 EER | 9.0 EER
SPVHP (cooling mode), nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  | 9.2 EER | 9.2 EER
|  |  | >30,000 and ≤36,000 Btu/h |  | 9.0 EER | 9.0 EER
SPVHP (heating mode) nonweatherized space constrained
|  |  | ≤30,000 Btu/h |  | 3.0 COP | 3.0 COP
|  |  | >30,000 and ≤36,000 Btu/h |  | 3.0 COP | 3.0 COP
| Electrically Operated Room Air Conditioners |  |  | Requirements
|  | With louvered sides | <6,000 Btu/h |  | 9.7 SEER | 9.7 SEER
|  |  | ≥6,000 and <8,000 Btu/h |  | 9.7 EER | 9.7 EER
|  |  | ≥8,000 and <14,000 Btu/h |  | 9.8 EER | 9.8 EER
|  |  | ≥14,000 and <20,000 Btu/h |  | 9.7 EER | 9.7 EER
|  |  | ≥20,000 Btu/h |  | 8.5 EER | 8.5 EER
|  | Without louvered sides | <8,000 Btu/h |  | 9.0 EER | 9.0 EER
|  |  | ≥8,000 and <20,000 Btu/h |  | 8.5 EER | 8.5 EER
|  |  | ≥20,000 Btu/h |  | 8.5 EER | 8.5 EER
|  | Casement only |  |  | 8.7 EER | 8.7 EER
|  | Casement-slider |  |  | 9.5 EER | 9.5 EER
| Electrically Operated Room Heat Pumps |  |  | Requirements
|  | With louvered side | <20,000 Btu/h |  | 9.0 EER | 9.0 EER
|  |  | ≥20,000 Btu/h |  | 8.5 EER | 8.5 EER
|  | Without louvered sides | <14,000 Btu/h |  | 8.5 EER | 8.5 EER
|  |  | ≥14,000 Btu/h |  | 8.0 EER | 8.0 EER
Warm Air Furnaces and Combination Warm Air Furnaces/Air Conditioning Units
|  |  | Gas-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 78% AFUE or 80% Et | 78% AFUE or 80% Et
|  |  | Gas-Fired ≥225,000 Btu/h | 80% Et | 80% Et | 80% Et
|  |  | Oil-Fired <225,000 Btu/h | 78% AFUE or 80% Et | 78% AFUE or 80% Et | 78% AFUE or 80% Et
|  |  | Oil-Fired ≥225,000 Btu/h | 81% Et | 81% Et | 81% Et
Warm Air Duct Furnaces
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec
Warm Air Unit Heaters
|  |  | Gas-Fired | 80% Ec | 80% Ec | 80% Ec
|  |  | Oil-Fired | 80% Ec | 80% Ec | 80% Ec
Boilers, Gas-Fired
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 82% AFUE | 82% AFUE
|  | <300,000 Btu/h, Steam |  | 75% AFUE | 80% AFUE | 80% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 80% Et | 80% Et | 80% Et
|  | ≥300,000 & ≤2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et
|  | ≥300,000 & ≤2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 77% Et
|  | >2,500,000 Btu/h, Hot Water |  | 82% Ec | 82% Ec | 82% Ec
|  | >2,500,000 Btu/h, (Except Natural Draft) Steam |  | 79% Et | 79% Et | 79% Et
|  | >2,500,000 Btu/h, Natural Draft, Steam |  | 77% Et | 77% Et | 77% Et
Boilers, Oil-Fired
|  | <300,000 Btu/h, Hot Water |  | 80% AFUE | 84% AFUE | 84% AFUE
|  | <300,000 Btu/h, Steam |  | 80% AFUE | 82% AFUE | 82% AFUE
|  | ≥300,000 & ≤2,500,000 Btu/h, Hot Water |  | 82% Et | 82% Et | 82% Et
|  | ≥300,000 & ≤2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et
|  | >2,500,000 Btu/h, Hot Water |  | 84% Ec | 84% Ec | 84% Ec
|  | >2,500,000 Btu/h, Steam |  | 81% Et | 81% Et | 81% Et
Heat Rejection Equipment
|  | Propeller or Axial Fan Open-Circuit Cooling Towers |  | ≥38.2 gpm/hp | ≥40.2 gpm/hp | ≥40.2 gpm/hp
|  | Centrifugal Fan Open-Circuit Cooling Towers ≤1,100 gpm |  | ≥20.0 gpm/hp | ≥20.0 gpm/hp | ≥20.0 gpm/hp
|  | Centrifugal Fan Open-Circuit Cooling Towers >1,100 gpm |  |  | ≥20.0 gpm/hp | ≥20.0 gpm/hp
|  | Propeller or Axial Fan Closed-Circuit Cooling Towers |  | ≥14.0 gpm/hp | ≥14.0 gpm/hp | ≥16.1 gpm/hp
|  | Centrifugal Fan Closed-Circuit Cooling Towers |  | ≥7.0 gpm/hp | ≥7.0 gpm/hp | ≥7.0 gpm/hp
|  | Propeller or axial fan evaporative condensers (R-507A test fluid) |  |  | ≥157,000 Btu/h-hp | ≥157,000 Btu/h-hp
|  | Propeller or axial fan evaporative condensers (Ammonia test fluid) |  |  | ≥134,000 Btu/h-hp | ≥134,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (R-507A test fluid) |  |  | ≥135,000 Btu/h-hp | ≥135,000 Btu/h-hp
|  | Centrifugal fan evaporative condensers (Ammonia test fluid) |  |  | ≥110,000 Btu/h-hp | ≥110,000 Btu/h-hp
|  | Air-Cooled Condensers |  | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp | ≥176,000 Btu/h-hp
Heat Transfer Equipment
|  | Liquid-to-Liquid, plate type heat exchangers |  |  | NR | NR
| Air Conditioners and Condensing Units Serving Computer Rooms |  |  | Downflow/Upflow Units SCOP-127 | Downflow/Upflow Units SCOP-127 | Minimum Net SCOP
Air Cooled
|  |  | <65,000 Btu/h | 2.20 / 2.09 | 2.20 / 2.09
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.09
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.45
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.99
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.35
|  |  | ≥240,000 Btu/h | 1.90 / 1.79 | 1.90 / 1.79
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.85
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.79
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.15
Water Cooled
|  |  | <65,000 Btu/h | 2.60 / 2.49 | 2.60 / 2.49
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.5
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.25
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.7
|  |  | ≥65,000 & <240,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.2
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.6
|  |  | ≥240,000 Btu/h | 2.40 / 2.29 | 2.40 / 2.29
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.25
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.05
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.45
Water Cooled With Fluid Economizer
|  |  | <65,000 Btu/h | 2.55 / 2.44 | 2.55 / 2.44
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.45
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.6
|  |  | ≥65,000 & <240,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.15
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2.1
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.55
|  |  | ≥240,000 Btu/h | 2.35 / 2.24 | 2.35 / 2.24
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.2
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.05
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.4
Glycol Cooled
|  |  | <65,000 Btu/h | 2.50 / 2.39 | 2.50 / 2.39
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.3
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.4
|  |  | ≥65,000 & <240,000 Btu/h | 2.15 / 2.04 | 2.15 / 2.04
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 2.05
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.85
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.15
|  |  | ≥240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.95
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.75
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
Glycol Cooled With Fluid Economizer
|  |  | <65,000 Btu/h | 2.45 / 2.34 | 2.45 / 2.34
|  |  | <65,000 Btu/h Downflow Unit, Class 2 |  |  | 2.25
|  |  | <65,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 2.1
|  |  | <65,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 2
|  |  | <65,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.35
|  |  | ≥65,000 & <240,000 Btu/h | 2.10 / 1.99 | 2.10 / 1.99
|  |  | ≥65,000 & <240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.95
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥65,000 & <240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.75
|  |  | ≥65,000 & <240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
|  |  | ≥240,000 Btu/h | 2.05 / 1.94 | 2.05 / 1.94
|  |  | ≥240,000 Btu/h Downflow Unit, Class 2 |  |  | 1.9
|  |  | ≥240,000 Btu/h Upflow Unit-ducted, Class 2 |  |  | 1.8
|  |  | ≥240,000 Btu/h Upflow Unit-nonducted, Class 1 |  |  | 1.7
|  |  | ≥240,000 Btu/h Horizontal-flow Unit, Class 3 |  |  | 2.1
Variable Refrigerant Flow (VRF) Systems
|  | VFR Multi-Split Air Conditioners, Air Cooled |  |  |  | as of 1/1/2017
|  |  | <65,000 Btu/h, All Heating Section | 13.0 SEER | 13.0 SEER | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section | 11.2 EER 13.5 IEER | 11.2 EER 12.5 IEER | 11.2 EER 15.5 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section | 11.0 EER 12.9 IEER | 11.0 EER 12.3 IEER | 11.0 EER 14.9 IEER
|  |  | ≥240,000 Btu/h, Electric Resistance (or None) Heating Section | 10.0 EER 11.6 IEER | 10.0 EER 11.1 IEER | 10.0 EER 13.9 IEER
|  | VFR Multi-Split Heat Pumps, Air Cooled (Cooling Mode) |  |  |  | as of 1/1/2017
|  |  | <65,000 Btu/h, All Heating Section | 13.0 SEER | 13.0 SEER | 13.0 SEER
|  |  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section | 11.0 EER 12.9 IEER | 11.0 EER 12.3 IEER | 11.0 EER 14.6 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section | 10.6 EER 12.3 IEER | 10.6 EER 11.8 IEER | 10.6 EER 13.9 IEER
|  |  | ≥240,000 Btu/h, Electric Resistance (or None) Heating Section | 9.5 EER 11.0 IEER | 9.5 EER 10.6 IEER | 9.5 EER 12.7 IEER
|  | VFR Multi-Split with Heat Recovery Heat Pumps, Air Cooled (Cooling Mode) |  |  |  | as of 1/1/2017
|  |  | ≥65,000 & <135,000 Btu/h, Electric Resistance (or None) Heating Section | 10.8 EER 12.7 IEER | 10.8 EER 12.1 IEER | 10.8 EER 14.4 IEER
|  |  | ≥135,000 & <240,000 Btu/h, Electric Resistance (or None) Heating Section | 10.4 EER 12.1 IEER | 10.4 EER 11.6 IEER | 10.4 EER 13.7 IEER
|  |  | ≥240,000 Btu/h, Electric Resistance (or None) Heating Section | 9.3 EER 10.8 IEER | 9.3 EER 10.4 IEER | 9.3 EER 12.5 IEER
|  | VFR Multi-Split Heat Pumps, Water Source (Cooling Mode) 86º Entering Water |  |  |  | as of 1/1/2018
|  |  | <65,000 Btu/h, All Heating Section | 12.0 EER | 12.0 EER | 12.0 EER 16.0 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All Heating Section | 12.0 EER | 12.0 EER | 12.0 EER 16.0 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section | 10.0 EER | 10.0 EER | 10.0 EER 14.0 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 10.0 EER 12.0 IEER
|  | VFR Multi-Split Heat Pumps with Heat Recovery, Water Source (Cooling Mode) 86º Entering Water |  |  |  | as of 1/1/2018
|  |  | <65,000 Btu/h, All Heating Section | 11.8 EER | 11.8 EER | 11.8 EER 15.8 IEER
|  |  | ≥65,000 & <135,000 Btu/h, All Heating Section | 11.8 EER | 11.8 EER | 11.8 EER 15.8 IEER
|  |  | ≥135,000 & <240,000 Btu/h, All Heating Section | 9.8 EER | 9.8 EER | 9.8 EER 13.8 IEER
|  |  | ≥240,000 Btu/h, All Heating Section |  |  | 9.8 EER 11.8 IEER
VFR Multi-Split Heat Pumps, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All Heating Section | 16.2 EER | 16.2 EER | 16.2 EER
|  |  | ≥135,000 Btu/h, All Heating Section | 13.8 EER | 13.8 EER | 13.8 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Groundwater Source (Cooling Mode) 59º Entering Water
|  |  | <135,000 Btu/h, All Heating Section | 16.0 EER | 16.0 EER | 16.0 EER
|  |  | ≥135,000 Btu/h, All Heating Section | 13.6 EER | 13.6 EER | 13.6 EER
VFR Multi-Split Heat Pumps, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All Heating Section | 13.4 EER | 13.4 EER | 13.4 EER
|  |  | ≥135,000 Btu/h, All Heating Section | 11.0 EER | 11.0 EER | 11.0 EER
VFR Multi-Split Heat Pumps with Heat Recovery, Ground Source (Cooling Mode) 77º Entering Water
|  |  | <135,000 Btu/h, All Heating Section | 13.2 EER | 13.2 EER | 13.2 EER
|  |  | ≥135,000 Btu/h, All Heating Section | 10.8 EER | 10.8 EER | 10.8 EER
VFR Multi-Split Heat Pumps, Air Cooled (Heating Mode)
|  |  | <65,000 Btu/h (Cooling Capacity) | 7.7 HSPF | 7.7 HSPF | 7.7 HSPF
≥65,000 & <135,000 Btu/h (Cooling Capacity)
|  |  | 47ºF db / 43ºF wb | 3.3 COP | 3.3 COP | 3.3 COP
|  |  | 17ºF db / 15ºF wb | 2.25 COP | 2.25 COP | 2.25 COP
≥135,000 (Cooling Capacity)
|  |  | 47ºF db / 43ºF wb | 3.2 COP | 3.2 COP | 3.2 COP
|  |  | 17ºF db / 15ºF wb | 2.05 COP | 2.05 COP | 2.05 COP
|  | VFR Multi-Split Heat Pumps, Water Source (Heating Mode) 68º Entering Water |  |  |  | as of 1/1/2018
|  |  | <65,000 Btu/h (Cooling Capacity) |  |  | 4.3 COP
|  |  | ≥65,000 & <135,000 Btu/h (Cooling Capacity) | 4.2 COP | 4.2 COP | 4.3 COP
|  |  | ≥135,000 & <240,000 Btu/h (Cooling Capacity) | 3.9 COP | 3.9 COP | 4.0 COP
|  |  | ≥240,000 Btu/h (Cooling Capacity) |  |  | 3.9 COP
VFR Multi-Split Heat Pumps, Groundwater Source (Heating Mode) 50º Entering Water
|  |  | <135,000 Btu/h (Cooling Capacity) | 3.6 COP | 3.6 COP | 3.6 COP
|  |  | ≥135,000 Btu/h (Cooling Capacity) | 3.3 COP | 3.3 COP | 3.3 COP
VFR Multi-Split Heat Pumps, Ground Source (Heating Mode) 32º Entering Water
|  |  | <135,000 Btu/h (Cooling Capacity) | 3.1 COP | 3.1 COP | 3.1 COP
|  |  | ≥135,000 Btu/h (Cooling Capacity) | 2.8 COP | 2.8 COP | 2.8 COP
Vapor Compression Based Indoor Pool Dehumidifiers
|  |  | Single package indoor without air-cooled condenser (with or without economizer) |  |  | 3.5 MRE
|  |  | Single package water-cooled (with or without economizer) |  |  | 3.5 MRE
|  |  | Single package air-cooled (with or without economizer) |  |  | 3.5 MRE
|  |  | Split system air-cooled (with or without economizer) |  |  | 3.5 MRE
Dedicated Outdoor Air Units
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, without Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 4.9 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.0 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 2.7 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 4.8 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.0 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.0 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 2.0 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 3.5 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 3.5 ISCOP
Direct Expansion, Electrically Operated, Single-Package and Remote Condenser, with Energy Recovery
|  |  | Air cooled (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Air source heat pump (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Water cooled with cooling tower condenser water (dehumidification mode) |  |  | 5.3 ISMRE
|  |  | Water cooled with chilled water (dehumidification mode) |  |  | 6.6 ISMRE
|  |  | Air source heat pump (heating mode) |  |  | 3.3 ISCOP
|  |  | Closed loop ground source heat pump (dehumidification mode) |  |  | 5.2 ISMRE
|  |  | Ground-water source heat pump (dehumidification mode) |  |  | 5.8 ISMRE
|  |  | Water source heat pump (dehumidification mode) |  |  | 4.8 ISMRE
|  |  | Closed loop ground source heat pump (heating mode) |  |  | 3.8 ISCOP
|  |  | Ground-water source heat pump (heating mode) |  |  | 4.0 ISCOP
|  |  | Water source heat pump (heating mode) |  |  | 4.8 ISCOP
HVAC Controls and Diagnostics
Zone Thermostatic Controls
|  |  | Zone | Within Each | Within each | Within each
|  |  | Dwelling Unit | Single Zone | Single zone | Single zone
|  |  | Perimeter System | per Each Exterior Exposure per Orientation | Per each exterior exposure per orientation | Per each exterior exposure per orientation
|  |  | Dead Band Between Heating & Cooling | 5º | ≥5º | ≥5º
|  | Set Point Overlap Restriction |  | Yes | Set point overlap restriction where separate heating & cooling controls located in zone | Set point overlap restriction where separate heating & cooling controls located in zone
Off-Hour Controls
|  |  | Automatic setback and shutdown |  | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor | 7 daily schedules per week with 2 hour maximum manual override or occupancy sensor
|  |  | Automatic Shutdown | Required | Required | Required
|  |  | Setback Controls | Required | Required | Required
|  |  | Setback capabilities |  | Adjustable heating ≥10° below occupied heating setpoint | Adjustable heating ≥10° below occupied heating setpoint
[5 empty] | Adjustable cooling ≥5° above occupied cooling setpoint or to prevent high space humidity levels | Adjustable cooling ≥5° above occupied cooling setpoint or to prevent high space humidity levels
|  |  | Optimum Start Controls | Required in systems >10,000 cfm total design supply air capacity | In individual heating and cooling systems with setback controls and DDC | In individual heating and cooling systems with setback controls and DDC
|  |  | Zone Isolation | Required | Required for nonsimultaneously occupied zones | Required for nonsimultaneously occupied zones
[5 empty] | Isolation zones <25,000 sf or 1 floor | Isolation zones <25,000 sf or 1 floor
[5 empty] | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area | Automatically shut off supply of conditioned air & outdoor air to and exhaust air from the isolation area
|  |  | Automatic HVAC Controls in Hotel/Motel Guest Rooms |  |  | In hotels & motels with >50 guest rooms
Automatically raise occupant set point ≥4° in cooling mode within 30 minutes of occupants leaving guest room
Automatically lower occupant set point ≥4° in heatling mode within 30 minutes of occupants leaving guest room
When room is unrented & unoccupied, automatically reset to ≥80° in cooling mode & to ≤60° in heating mode
Within 30 of occupants leaving room, automatically turn off ventilation and exhaust fans or
Automatically shut off supply of outdoor air & shut off exhaust air
Captive key card systems permitted to be used to comply
|  |  | Exceptions to Off-Hour Controls | Continuous Operation | Continuous Operation | Continuous Operation
|  |  |  | Systems <15,000 Btu/h with readily accessible manual on/off | Systems <15,000 Btu/h with readily accessible manual on/off | Systems <15,000 Btu/h with readily accessible manual on/off
Ventilation System Controls
|  |  | Stair and Elevator Shaft Vents, Buildings ≥3 Stories | Motorized Dampers w/ 4 cfm/sf Maximum Leakage Rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Stair and Elevator Shaft Vents, Buildings <3 Stories | Motorized Dampers w/ 4 cfm/sf Maximum Leakage Rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Outdoor Air Supply & Exhaust, Buildings ≥3 Stories | Motorized Dampers w/ 4 cfm/sf Maximum Leakage Rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Outdoor Air Supply, Buildings <3 Stories | Motorized Dampers w/ 4 cfm/sf Maximum Leakage Rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate | Motorized dampers w/ 4 cfm/sf maximum leakage rate
|  |  | Exhaust/Relief, Buildings <3 Stories | Gravity Dampers w/ 20 cfm/sf Maximum Leakage Rate | Gravity dampers w/ 20 cfm/sf maximum leakage rate | Gravity dampers w/ 20 cfm/sf maximum leakage rate
|  |  | Shutoff Damper Controls | Required for Motorized Dampers | Required for motorized dampers | Required for motorized dampers
|  |  | Ventilation Fans >3/4 hp | Automatic Off-Hour Shutdown Required | Automatic off-hour shutoff required | Automatic off-hour shutoff required
|  |  | Enclosed Parking Garage Ventilation | Automatic air flow rate control to ≤50% based on contaminant levels | Automatic air flow rate control to ≤50% based on contaminant levels | Automatic air flow rate control to ≤50% based on contaminant levels
|  |  |  | Exceptions: | Exceptions: | Exceptions:
|  |  |  | 1. Garages <30,000 sf without mechanical heating or cooling | 1. Garages <30,000 sf without mechanical heating or cooling | 1. Garages <30,000 sf without mechanical heating or cooling
|  |  |  | 2. Garages with ventilation system >1,500 sf/hp | 2. Garages with ventilation system >1,500 sf/hp | 2. Garages with ventilation system >1,500 sf/hp
Heat Pump Auxiliary Heat Control
|  |  | Prevent Internal Electric Resistance Heater Operation when Heating Load Can Be Met by Heat Pump Alone | Required | Required | Required
Humidification and Dehumidification
|  |  | Prevention fossil fuel or electricity use |  | To produce RH >30% by humidification | To produce RH >30% by humidification
[5 empty] | To produce RH 60% by dehumidification | To produce RH 60% by dehumidification
|  |  | Prevention of Simultaneous Operation | Required | Required | Required
Freeze Protection and Snow/Ice Melting Systems
|  |  | Automatic Shutoff for Freeze Protection | Above 40º Outside Air Temperature | >40º outside air temperature or when conditions of protected fluid will prevent freezing | >40º outside air temperature or when conditions of protected fluid will prevent freezing
|  |  | Automatic Shutoff for Melting Systems | Above 50º Pavement Temperature & No Precipitation plus Control for Above 40º Outdoor Air Temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature | >50º pavement temperature & no precipitation plus automatic or manual control for >40º outdoor air temperature
Ventilation Controls For High-Occupancy
|  |  | Means to Automatically Reduce Outside Air Intake during Partial Occupancy (Demand Control Ventilation) | Required for Spaces >500 sf & Design Occupancy >40 Persons per 1,000 sf & Served By Defined HVAC System | Required for spaces >500 sf & design occupancy ≥25 persons per 1,000 sf & served by defined HVAC system | Required for spaces >500 sf & design occupancy ≥25 persons per 1,000 sf & served by defined HVAC system
Vestibule Heating and Cooling
|  |  | Heating Controls |  | Shut off heating when outdoor air temperature >45° | Shut off heating when outdoor air temperature >45°
[5 empty] | Thermostat located in vestibule | Thermostat located in vestibule
[5 empty] | Thermostat setpoint limit ≤60° | Thermostat setpoint limit ≤60°
|  |  | Cooling Controls |  |  | Thermostat located in vestibule
Thermostat setpoint limit ≥85°
Direct Digital Control (DDC) Required Applications
New Buildings
|  |  | Air-handling system and all zones served by system |  | Individual system serving >3 zones & with fan system bhp ≥10 hp | Individual system serving >3 zones & with fan system bhp ≥10 hp
|  |  | Chilled-water plant and all coils and terminal units served by system |  | Individual plants supplying >3 zones with design cooling capacity ≥300,000 Btu/h | Individual plants supplying >3 zones with design cooling capacity ≥300,000 Btu/h
|  |  | Hot-water plant and all coils and terminal units served by system |  | Individual plants supplying >3 zones with design heating capacity ≥300,000 Btu/h | Individual plants supplying >3 zones with design heating capacity ≥300,000 Btu/h
Direct Digital Control (DDC) Required Applications
Alteration or Addition
|  |  | Zone terminal unit |  | Where existing zones served by same air handling, chilled-water, or hot-water system have DDC | Where existing zones served by same air handling, chilled-water, or hot-water system have DDC
|  |  | Air-handling system or fan coil |  | Where existing air-handling system(s) and fan coil(s) served by same chilled- or hot-water plant have DDC | Where existing air-handling system(s) and fan coil(s) served by same chilled- or hot-water plant have DDC
|  |  | New air-handling system and all new zones served by the system |  | Individual systems with fan system bhp ≥10 hp and supplying >3 zones and >75% zones are new | Individual systems with fan system bhp ≥10 hp and supplying >3 zones and >75% zones are new
|  |  | New or upgraded chilled-water plant |  | Where all chillers are new and plant design cooling capacity ≥300,000 Btu/h | Where all chillers are new and plant design cooling capacity ≥300,000 Btu/h
|  |  | New or upgraded hot-water plant |  | Where all boilers are new and plan design heating capacity ≥300,000 Btu/h | Where all boilers are new and plan design heating capacity ≥300,000 Btu/h
Direct Digital Control (DDC) Requirements
|  |  | Control capabilities |  | Monitoring zone & system demand for fan pressure, pump pressure, heating and cooling | Monitoring zone & system demand for fan pressure, pump pressure, heating and cooling
[5 empty] | Transferring zone & system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers | Transferring zone & system demand information from zones to air distribution system controllers and from air distribution systems to heating and cooling plant controllers
[5 empty] | Automatically detecting those zones and systems that may be excessively driving reset logic and generate alarm or other indication to system operator | Automatically detecting those zones and systems that may be excessively driving reset logic and generate alarm or other indication to system operator
[5 empty] | Readily allowing operator removal of zone(s) from reset algorithm | Readily allowing operator removal of zone(s) from reset algorithm
|  |  | DDC Display |  | Where required for new buildings, capable of trending and graphically displaying input and output points | Where required for new buildings, capable of trending and graphically displaying input and output points
Chilled-Water Plant Monitoring
|  |  | Monitoring |  |  | For new electric-motor-driven chilled water plants
>1,500 tons peak cooling capacity for water-cooled plants
>860 tons peak cooling capacity air-cooled plants
Measure electric energy use and chilled-water plant efficieny
|  |  | Recording and Reporting of electrical energy use efficiency |  |  | Trended every 15 minutes
Grapically display to include:
hourly data
daily data
monthly data
annual data
Store data ≥36 months
|  | Economizer Fault Detection and Diagnostics (FDD) |  |  |  | For air-cooled direct-expansion cooling units
|  |  | Pemanently installed temperature sensors |  |  | Outdoor air
Supply air
Return air (where required for economizer control)
|  |  | Display |  |  | Value of each sensor
|  |  | FDD system or unit controls |  |  | Free cooling available
|  |  | to provide system status |  |  | Economizer enbled
Compressor enabled
Heating enabled
Mixed-air low-lomit cycle active
|  |  | FDD system or unit controls have provisions to |  |  | Manually initiate each operating mode for testing & verification
|  |  | Fault detection capabilities |  |  | Air temperature sensor failure/fault
Not economizing
Economizing when should not
Damper not modulating
Excess outdoor air
HVAC Construction and Insulation
|  | Heating Ducts Only, Located In |  |  |  | (Return and Supply Ducts)
|  |  | Exterior | R-6 | R-6 | R-12
|  |  | Ventilated Attic | R-3.5 | R-3.5
|  |  | Unvented Attic Above Ceiling Insulation | none | none
|  |  | Unvented Attic with Roof Insulation | none | none
|  |  | Unconditioned Space | none | none | R-6
|  |  | Indirectly Conditioned Space | none | none | R-1.9
|  |  | Buried | R-3.5 | R-3.5 | R-6
|  | Cooling Ducts Only, Located In |  |  |  | (Return and Supply Ducts)
|  |  | Exterior | R-3.5 | R-3.5 | R-8
|  |  | Ventilated Attic | R-1.9 | R-1.9
|  |  | Unvented Attic Above Ceiling Insulation | R-3.5 | R-3.5
|  |  | Unvented Attic with Roof Insulation | R-1.9 | R-1.9
|  |  | Unconditioned Space | R-1.9 | R-1.9 | R-6
|  |  | Indirectly Conditioned Space | none | none | R-1.9
|  |  | Buried | none | none | R-6
|  | Return Duct for Cooling and Heating Only System, Located In |  |  |  | (Return and Supply Ducts)
|  |  | Exterior | R-3.5 | R-3.5 | R-8
|  |  | Ventilated Attic | R-3.5 | R-3.5
|  |  | Unvented Attic Above Ceiling Insulation | R-3.5 | R-3.5
|  |  | Unvented Attic with Roof Insulation | none | none
|  |  | Unconditioned Space | none | none | R-6
|  |  | Indirectly Conditioned Space | none | none | R-1.9
|  |  | Buried | none | none | R-6
|  | Combined Heating and Cooling Supply Ducts, Located In |  |  |  | (Return and Supply Ducts)
|  |  | Exterior | R-6 | R-6 | R-12
|  |  | Ventilated Attic | R-6 | R-6
|  |  | Unvented Attic Above Ceiling Insulation | R-6 | R-6
|  |  | Unvented Attic with Roof Insulation | R-1.9 | R-1.9
|  |  | Unconditioned Space | R-3.5 | R-3.5 | R-6
|  |  | Indirectly Conditioned Space | none | none | R-1.9
|  |  | Buried | R-3.5 | R-3.5 | R-6
|  | Return Duct for Combined Heating and Cooling System, Located In |  |  |  | (Return and Supply Ducts)
|  |  | Exterior | R-3.5 | R-3.5 | R-12
|  |  | Ventilated Attic | R-3.5 | R-3.5
|  |  | Unvented Attic Above Ceiling Insulation | R-3.5 | R-3.5
|  |  | Unvented Attic with Roof Insulation | none | none
|  |  | Unconditioned Space | none | none | R-6
|  |  | Indirectly Conditioned Space | none | none | R-1.9
|  |  | Buried | none | none | R-6
Heating System (Steam, Steam Condensate and Hot Water) Pipe Insulation
>350ºF Fluid Temperature & 0.32 - 0.34 Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 4.5" | 4.5" | 4.5"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 5.0" | 5.0" | 5.0"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 5.0" | 5.0" | 5.0"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 5.0" | 5.0" | 5.0"
|  |  | ≥8" Nominal Pipe or Tube Size | 5.0" | 5.0" | 5.0"
251-350ºF Fluid Temperature & 0.29 - 0.32 Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 3.0" | 3.0" | 3.0"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 4.0" | 4.0" | 4.0"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 4.5" | 4.5" | 4.5"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 4.5" | 4.5" | 4.5"
|  |  | ≥8" Nominal Pipe or Tube Size | 4.5" | 4.5" | 4.5"
201-250ºF Fluid Temperature & 0.27 - 0.30 Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 2.5" | 2.5" | 2.5"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 2.5" | 2.5" | 2.5"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 2.5" | 2.5" | 2.5"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 3.0" | 3.0" | 3.0"
|  |  | ≥8" Nominal Pipe or Tube Size | 3.0" | 3.0" | 3.0"
141-200ºF Fluid Temperature & 0.25 - 0.29 Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 2.0" | 2.0" | 2.0"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 2.0" | 2.0" | 2.0"
|  |  | ≥8" Nominal Pipe or Tube Size | 2.0" | 2.0" | 2.0"
105-140ºF Fluid Temperature & 0.22 - 0.28 Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
|  |  | ≥8" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
Sensible Heating Panel Insulation
|  |  | Insulation for all thermally ineffective panel surfaces including U-bends and headers |  |  | R-3.5
|  |  | Insulation on bottom surface of floor structures incorporating radiant heating |  |  | R-3.5
Domestic and Service Hot Water System Pipe Insulation
|  | 105+ºF Fluid Temperature & 0.22 - 0.28 Insulation Conductivity |  |  | Included in Table 6.8.3-1 above(same fluid temperature) | Included in Table 6.8.3-1 above(same fluid temperature)
|  |  | <1" Nominal Pipe or Tube Size | 1"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 1"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 1.5"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 1.5"
|  |  | ≥8" Nominal Pipe or Tube Size | 1.5"
Cooling Systems (Chilled Water, Brine, and Refrigerant) Pipe Insulation
40-60ºF Fluid Temperature & 0.22 - 0.28 (0.21 - 0.27 in 2010) Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 0.5" | 0.5" | 0.5"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 0.5" | 0.5" | 0.5"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | ≥8" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
<40ºF Fluid Temperature & 0.22 - 0.28 (0.20 - 0.26 in 2010) Insulation Conductivity
|  |  | <1" Nominal Pipe or Tube Size | 0.5" | 0.5" | 0.5"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 1.0" | 1.0" | 1.0"
|  |  | ≥8" Nominal Pipe or Tube Size | 1.5" | 1.5" | 1.5"
Duct (Ductwork and Plennum) Sealing
|  |  | Ductwork and All Plenums With Presure Class Ratings | Seal Class A | Seal Class A | Seal Class A
Duct Leakage Tests
|  |  | Outside Ductwork | Required for All | Required for All | Required for All
|  |  | >3 in. w.c.. Operating Static Pressure | Required Leak Tests for no less than 25% of Total Installed Duct Area | Required Leak Tests for no less than 25% of Total Installed Duct Area | Required Leak Tests for no less than 25% of Total Installed Duct Area
Economizers
Required for Each Cooling System
|  |  | Individual fan-cooling units with supply capacity | ≥54,000 Btu/h | ≥54,000 Btu/h | ≥54,000 Btu/h
|  |  | Chilled-water cooling system without fan or uses induced airflow with total cooling capacity |  |  | ≥1,400,000 Btu/h
|  | Computer Room | Required | Fan-Cooling Units ≥135,000 Btu/h | Fan-Cooling Units ≥135,000 Btu/h | Required or alternate compliance in computer room Power Usage Effectiveness (PUE)
|  |  | Exceptions | Where ≥75% Design Load Serves Defined Conditions | Systems primarily serving computer rooms | Systems primarily serving computer rooms
[5 empty] | a) Total design cooling load of all computer rooms <3,000,000 Btu/h & building served by central chiller plant | a) Total design cooling load of all computer rooms <3,000,000 Btu/h & building served by central chiller plant
[5 empty] | b) Room design cooling load <600,000 Btu/h and building served by centralized chiller plant | b) Room design cooling load <600,000 Btu/h and building served by centralized chiller plant
[5 empty] | c) Cooling towers not allowed by water authority | c) Cooling towers not allowed by water authority
[5 empty] | d) <600,000 Btu/h computer-room cooling equipment added to existing building | d) <600,000 Btu/h computer-room cooling equipment added to existing building
[5 empty] | ≥75% dedicated systems serve: | ≥75% dedicated systems serve:
[5 empty] | a) Spaces classified as essential facility | a) Spaces classified as essential facility
[5 empty] | b) Tier IV space | b) Tier IV space
[5 empty] | c) Space classified as critical operations power systems | c) Space classified as critical operations power systems
[5 empty] | d) Spaces where core financial transactions are cleared & settled | d) Spaces where core financial transactions are cleared & settled
Air Economizer
|  |  | Capacity | Outside Air Up To 100% of Design Supply Air Quantity | Modulating outside air up to 100% of design supply air quantity | Modulating outside air up to 100% of design supply air quantity
|  |  | Alternate Compliance to Airside Economizer for Unitary Equipment | 49% Efficiency Improvement | 49% Efficiency Improvement | 49% Efficiency Improvement
|  |  | Air Economizer Control Signal | Sequenced with Mechanical Cooling Equipment | Sequenced with mechanical cooling equipment | Sequenced with mechanical cooling equipment
[5 empty] | Not controlled by only mixed-air temperature | Not controlled by only mixed-air temperature
[5 empty] | Not increase heating energy use during normal operation | Not increase heating energy use during normal operation
[5 empty] | Not capable of creating a false load | Not capable of creating a false load
[5 empty] | Prevent preheat whenever mechanical cooling, including economizer operation, is occurring | Prevent preheat whenever mechanical cooling, including economizer operation, is occurring
[5 empty] | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F | Interlocked with mechanical cooling so outdoor air damper does not begin to close until leaving air temperature <45°F
|  |  | Stages of mechanical cooling for direct expansion (DX) units controlled by space temperature |  | ≥2 stages for units ≥65,000 Btu/h | ≥2 stages for units ≥65,000 Btu/h
Direct expansion (DX) cooling state stages requirements for modulating airflow units
|  |  | ≥65,000 and <240,000 Btu/h |  | ≥3 stages and ≤35% of full load compressor displacement | ≥3 stages and ≤35% of full load compressor displacement
|  |  | ≥240,000 Btu/h |  | ≥4 stages and ≤25% of full load compressor displacement | ≥4 stages and ≤25% of full load compressor displacement
|  |  | Air Economizer High Limit Shutoff | Reduce Outside Air To Minimum When It No Longer Reduces Cooling Energy Usage | Reduce outside air to minimum when it no longer reduces cooling energy usage | Reduce outside air to minimum when it no longer reduces cooling energy usage
|  |  | Air economizer dampers (return, exhaust/relief, outdoor air) |  | ≤4 cfm/sf air leakage rate | ≤4 cfm/sf air leakage rate
|  | Water economizer (Fluid economizer in 2016) |  | Provide Up To 100% of Cooling Load When Outside Air Is ≤50ºF db/≤45ºF wb With | Provide up to 100% of cooling load when outside air ≤50ºF db/≤45ºF wb | Provide up to 100% of cooling load when outside air ≤50ºF db/≤45ºF wb
|  |  |  | Defined Exceptions For Computer Rooms | Define exceptions for computer rooms with other economizers | Define exceptions for computer rooms with other economizers
[5 empty] | Required for systems (required to have economizer) with hydronic cooling and humidification system designed to maintain inside dew-point temperatures >35° | Required for systems (required to have economizer) with hydronic cooling and humidification system designed to maintain inside dew-point temperatures >35°
|  |  | Water Economizer Pressure Drop | <15 ft. or Secondary Loop | <15 ft. or Secondary Loop | <15 ft. or Secondary Loop
|  |  | Water Economizer Control | Integrated with Mechanical Equipment To Provide Partial Cooling | Integrated with Mechanical Equipment To Provide Partial Cooling | Integrated with Mechanical Equipment To Provide Partial Cooling
|  |  | Economizer Control | Not Increase Heating Energy Use During Normal Operation
Simultaneous Heating and Cooling Limitation
|  | Zone Thermostatic Controls |  | Capability to Sequence Supply | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled | Prevent reheating, recooling and mixing or simultaneously supplying air that has been previously heated or cooled
[5 empty] | Exception: | Exception:
[5 empty] | 1) 30% of maximum supply air to each zone for zones without DDC | 1) 30% of maximum supply air to each zone for zones without DDC
[5 empty] | 2) Minimum ventilation requirements | 2) Minimum ventilation requirements
[5 empty] | 3) Any higher rate demonstrated to reduce overall system annual energy use | 3) Any higher rate demonstrated to reduce overall system annual energy use
[5 empty] | 4) Airflow rate required to comply with applicable code or accreditation standards | 4) Airflow rate required to comply with applicable code or accreditation standards
|  |  | VAV control requirement before reheating, recooling or mixing takes place |  | Exception: | Exception:
[5 empty] | Zones with DDC, comply with all of: | Zones with DDC, comply with all of:
[5 empty] | 1) Airflow rate in dead band does not exceed larger of: | 1) Airflow rate in dead band does not exceed larger of:
[5 empty] | 1a) 20% zone design peak supply rate | 1a) 20% zone design peak supply rate
[5 empty] | 1b)Minimum ventilation requirements | 1b)Minimum ventilation requirements
[5 empty] | 1c) Any higher rate demonstrated to reduce overall system annual energy use | 1c) Any higher rate demonstrated to reduce overall system annual energy use
[5 empty] | 1d) Airflow rate required to comply with applicable code or accreditation standards | 1d) Airflow rate required to comply with applicable code or accreditation standards
[5 empty] | 2) Reheated, recooled or mixed air flow rate <50% zone design peak supply rate | 2) Reheated, recooled or mixed air flow rate <50% zone design peak supply rate
[5 empty] | 3) First stage of heating modulates zone supply air temperature to maximum setpoint while airflow is maintained at dead band flow rate | 3) First stage of heating modulates zone supply air temperature to maximum setpoint while airflow is maintained at dead band flow rate
[5 empty] | 4) Second stage of heating modulates airflow rate to heating maximum flow rate | 4) Second stage of heating modulates airflow rate to heating maximum flow rate
|  |  | Supply Air Temperature Reheat Limit | Where Allowed and Duct Openings > 6' Above Floor, Supply Air ≤20º Space Temperature Setpoint, Except During Warm-up | Where allowed and duct openings are >6' above floor, supply air temperature ≤20º space temperature setpoint, except during warm-up | Where allowed and duct openings are >6' above floor, supply air temperature ≤20º space temperature setpoint, except during warm-up
Hydronic System Controls
|  |  | Three-pipe systems | Prohibited | Prohibited | Prohibited
|  |  | Two-pipe changeover system | ≥15ºF Changeover Deadband with Outside Air Temperature | ≥15ºF Changeover Deadband with Outside Air Temperature | ≥15ºF Changeover Deadband with Outside Air Temperature
|  |  |  | 4 Hour Minimum Operation In One Mode | 4 Hour Minimum Operation In One Mode | 4 Hour Minimum Operation In One Mode
|  |  |  | Reset Controls with ≤30ºF Deadband Between Rejection and Addition | ≤30° F reset control for heating/cooling changeover point | ≤30° F reset control for heating/cooling changeover point
|  |  | Hydronic (Water Loop) Heat Pump Systems | ≥20° dead band between heat rejection and heat addition | ≥20° dead band between heat rejection and heat addition | ≥20° dead band between heat rejection and heat addition
|  |  |  | If closed-circuit cooling tower, Automatic valve to bypass all but minimal flow around tower or low leakage positive closure dampers on tower | If closed-circuit cooling tower, Automatic valve to bypass all but minimal flow around tower or low leakage positive closure dampers on tower | If closed-circuit cooling tower, Automatic valve to bypass all but minimal flow around tower or low leakage positive closure dampers on tower
|  |  |  | If open-circuit tower, Automatic valve to bypass all water flow around tower | If open-circuit tower, Automatic valve to bypass all water flow around tower | If open-circuit tower, Automatic valve to bypass all water flow around tower
|  |  |  | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop | If open-circuit tower with separate heat exchanger, Shutting down circulating pump on cooling tower loop
|  | Dehumidification |  | Humidistatic Controls To Prevent Reheating, Recooling or Mixing of Airstreams | Humidity controls to prevent reheating, recooling or mixing of airstreams | Humidity controls to prevent reheating, recooling or mixing of airstreams
Humidification
|  |  | Preheating Jackets Mounted in Airstream | Automatic Valve Shutoff | Automatic Valve Shutoff | Automatic Valve Shutoff
|  |  | Dispersion tube hot surface in airstream |  | Insulation ≥R-0.5 | Insulation ≥R-0.5
Air System Design and Control
|  | Fan Power Limitation |  |  | Fan systems >5 hp | Fan systems >5 hp
Option 1: Fan System Motor Nameplate hp
|  |  | Constant Volume | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011 | hp ≤CFMs x 0.0011
|  |  | Variable Volume | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015 | hp ≤CFMs x 0.0015
Option 2: Fan System bhp
|  |  | Constant Volume | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A | bhp ≤CFMs x 0.00094 + A
|  |  | Variable Volume | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A | bhp ≤CFMs x 0.0013 + A
|  |  | Single Zone Variable Air Volume | Comply With Constant Volume Fan Power Limitation | Comply with constant volume fan power limitation | Comply with constant volume fan power limitation
|  |  | Air Systems with Required Air Treatment or Filtering, or Heat Recovery, or Direct Evaporation | Device Adjustment Tables | Device adjustment tables | Device adjustment tables
|  |  | Motor Nameplate Horsepower, for each fan |  | Fan brake horsepower indicated on construction documents | Fan brake horsepower indicated on construction documents
[5 empty] | Selected motor not larger than first available motor size greater than | Selected motor not larger than first available motor size greater than
[5 empty] | 1) 1.5 x fan bhp for fans <6 bhp | 1) 1.5 x fan bhp for fans <6 bhp
[5 empty] | 2) 1.3 x fan bhp for fans ≥6 bhp | 2) 1.3 x fan bhp for fans ≥6 bhp
[5 empty] | 3)Systems complying with fan power limitation Option 1 | 3)Systems complying with fan power limitation Option 1
Fan efficiency
|  |  | Fan efficiency grade (FEG) |  | ≥67 | ≥67
|  |  | Total efficiency of fan @ design point of operation |  | Within 15 points of maximum total efficiency of the fan | Within 15 points of maximum total efficiency of the fan
Fan Airflow Control
|  |  | Fans with Variable-Speed Drive or | Fan Motors ≥10 hp
Vane-Axial Fans with Variable-Pitch Blades or
or Controls/Devices Resulting in <30% Demand at 50% Volume When Static Pressure = 1/3 Design
|  |  | Cooling systems required to vary air flow as function of load |  | For DX cooling system | For DX cooling system
[5 empty] | ≥65,000 Btu/h mechanical cooling capacity | ≥65,000 Btu/h mechanical cooling capacity
[5 empty] | For chilled water and evaporative cooling systems | For chilled water and evaporative cooling systems
[5 empty] | ≥¼ hp fan motor | ≥¼ hp fan motor
|  |  | Fan control for units that control mechanical cooling based on space temperature |  | ≥2 stages | ≥2 stages
[5 empty] | Low or minimum speed ≤66% of full speed | Low or minimum speed ≤66% of full speed
[5 empty] | Power draw at low or minimum speed ≤40% power at full speed | Power draw at low or minimum speed ≤40% power at full speed
[5 empty] | Low or minimum speed used during low cooling load and ventilation-only operation | Low or minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units that control space temperature by modulating airflow |  | Minimum speed ≤50% full speed | Minimum speed ≤50% full speed
[5 empty] | Power draw at minimum speed ≤30% power at full speed | Power draw at minimum speed ≤30% power at full speed
[5 empty] | Minimum speed used during low cooling load and ventilation-only operation | Minimum speed used during low cooling load and ventilation-only operation
|  |  | Fan control for units with airside economizer |  | ≥2 speeds during economizer operation | ≥2 speeds during economizer operation
|  | Single Zone Variable-Air-Volume Controls |  | Air-Handling and Fan-Coil Units with Chilled-Water Cooling Coils & Supply Fans ≥5 hp Shall Have Speed Control (Affects Dx Units ≥110,000 Btu/h after 1/1/12)
Variable Air Volume (VAV) Fan Control
|  |  | Static pressure reset | For Systems with Direct Digital Control of Individual Zone Boxes | For systems with direct digital control of individual zone boxes | For systems with direct digital control of individual zone boxes
[5 empty] | Control Capable of: | Control Capable of:
[5 empty] | 1) Automatic detection of any zone that excessively drives reset logic | 1) Automatic detection of any zone that excessively drives reset logic
[5 empty] | 2) Generating alarm | 2) Generating alarm
[5 empty] | 3) Allow operator to remove zone(s) from reset algorithm | 3) Allow operator to remove zone(s) from reset algorithm
|  |  | Return and Relief Fan Control |  |  | Relief air rate controlled
To directly maintain building pressure or
Indirectly through differential supply-return airflo tracking
Speed control so that
Total return/relief fan demand ≤30% total design power @ 50% total design fan flow
|  |  | Ventilation optimization control |  | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control | Automatic reduction of outdoor air in response to changes in system ventilation efficiency for multi-zone VAV systems with DDC and central control
|  |  | Parallel-Flow Fan-Powered VAV Terminal Control |  |  | Turn off terminal fan except when required for space heating or for ventilation
Turn on terminal fan as first stage heating before heating coil activation
During warmup or setback temperature control either
Operate terminal fan & heating coil without primary air or
Reverse terminal damper logic and heat with primary air
|  |  | Supply-air temperature reset |  | Required for Multiple Zone HVAC Systems | Required for Multiple Zone HVAC Systems
|  |  | Fractional hp fan motors (≥1/12 hp and <1 hp) |  | Electronically commutated motors or | Electronically commutated motors or
[5 empty] | ≥70% motor efficiency | ≥70% motor efficiency
[5 empty] | Have means to adjust speed for either balancing or remote control | Have means to adjust speed for either balancing or remote control
|  |  | Ventilation Design |  |  | Comply with 1 of
a) Minimum system outdoor air ≤135% required minimum outdoor air rate
b) Dampers, ductwork and controls that allow system to supply no more than required minimum outdoor air rate with single set-point adjustment
c) Exhaust air eneergy recovery
Hydronic System Design and Control
|  |  | Boiler Turndown |  | Minimum Turndown Ratio for boilers ≥1,000,000 Btu/h design input | Minimum Turndown Ratio for boilers ≥1,000,000 Btu/h design input
|  |  | ≥1,000,000 & ≤5,000,000 Btu/h |  | 3 to 1 | 3 to 1
|  |  | >5,000,000 & ≤10,000,000 Btu/h |  | 4 to 1 | 4 to 1
|  |  | >10,000,000 Btu/h |  | 5 to 1 | 5 to 1
|  |  | HVAC Pumping Systems With Modulating or Step Control Valves | Total Pump System Power >10 hp | Total Pump System Power >10 hp | Distribution systems containing ≥3 control valves
|  |  |  | Capable to Reduce Flow Rates to ≤50% of Design | Capable to reduce flow rates to 50% of design | Capable to reduce flow rates to ≤25% of design or minimum flow rate required by equipment manufacturer
|  |  |  | Exception: when minimum required flow < equipment minimum required flow & total pump system power ≤75 hp | Exception: when minimum required flow < equipment minimum required flow & total pump system power ≤75 hp
|  |  | Individual Pumps Serving Variable Flow Systems | Speed Control Required on Individual Chilled Water Pumps >5 hp | Speed control required on individual chilled water pumps >5 hp | Speed control required on individual pumps ≥7.5 hp
|  |  | Pump Isolation | Automatically Reduce Flow When Chiller/Boiler is Shut Down | Automatically shut off flow through chiller/boiler when chiller/boiler is shut down | Automatically shut off flow through chiller/boiler when chiller/boiler is shut down
|  |  | Chilled and Hot Water Temperature Reset Controls | For Systems >300,000 Btu/h Except Systems with Variable Flow | Systems >300,000 Btu/h Except systems with variable flow | Systems >300,000 Btu/h
|  |  | Hydronic (Water Loop) Heat Pump Systems | Two-Position Automatic Valve at Each Heat Pump | Two-position automatic valve at each hydronic heat pump | Two-position automatic valve at each hydronic heat pump
|  |  |  | Speed Control When Total Pump System Power >5 hp | Control or device that results ≤30% design wattage at 50% design flow when total pump system power >5 hp | Control or device that results ≤30% design wattage at 50% design flow when total pump system power >5 hp
Pipe Sizing
for all chilled water and condenser water piping
Nominal Size (inches)
|  |  | ≤2,000 Operating Hours per Year, Variable Flow/Variable Speed | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 180 gpm | 180 gpm | 180 gpm
|  |  | 3" | 270 gpm | 270 gpm | 270 gpm
|  |  | 4" | 530 gpm | 530 gpm | 530 gpm
|  |  | 5" | 620 gpm | 620 gpm | 620 gpm
|  |  | 6" | 1100 gpm | 1100 gpm | 1100 gpm
|  |  | 8" | 1800 gpm | 1800 gpm | 1800 gpm
|  |  | 10" | 2700 gpm | 2700 gpm | 2700 gpm
|  |  | 12" | 3800 gpm | 3800 gpm | 3800 gpm
|  |  | >12" | 13.0 fps | 13.0 fps | 13.0 fps
|  |  | ≤2,000 Operating Hours per Year, Other | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 120 gpm | 120 gpm | 120 gpm
|  |  | 3" | 180 gpm | 180 gpm | 180 gpm
|  |  | 4" | 350 gpm | 350 gpm | 350 gpm
|  |  | 5" | 410 gpm | 410 gpm | 410 gpm
|  |  | 6" | 740 gpm | 740 gpm | 740 gpm
|  |  | 8" | 1200 gpm | 1200 gpm | 1200 gpm
|  |  | 10" | 1800 gpm | 1800 gpm | 1800 gpm
|  |  | 12" | 2500 gpm | 2500 gpm | 2500 gpm
|  |  | >12" | 8.5 fps | 8.5 fps | 8.5 fps
|  |  | >2,000 and ≤4,400 Operating Hours per Year, Variable Flow/Variable Speed | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 130 gpm | 130 gpm | 130 gpm
|  |  | 3" | 210 gpm | 210 gpm | 210 gpm
|  |  | 4" | 400 gpm | 400 gpm | 400 gpm
|  |  | 5" | 470 gpm | 470 gpm | 470 gpm
|  |  | 6" | 860 gpm | 860 gpm | 860 gpm
|  |  | 8" | 1400 gpm | 1400 gpm | 1400 gpm
|  |  | 10" | 2000 gpm | 2000 gpm | 2000 gpm
|  |  | 12" | 2900 gpm | 2900 gpm | 2900 gpm
|  |  | >12" | 9.5 fps | 9.5 fps | 9.5 fps
|  |  | >2,000 and ≤4,400 Operating Hours per Year, Other | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 85 gpm | 85 gpm | 85 gpm
|  |  | 3" | 140 gpm | 140 gpm | 140 gpm
|  |  | 4" | 260 gpm | 260 gpm | 260 gpm
|  |  | 5" | 310 gpm | 310 gpm | 310 gpm
|  |  | 6" | 570 gpm | 570 gpm | 570 gpm
|  |  | 8" | 900 gpm | 900 gpm | 900 gpm
|  |  | 10" | 1300 gpm | 1300 gpm | 1300 gpm
|  |  | 12" | 1900 gpm | 1900 gpm | 1900 gpm
|  |  | >12" | 6.5 fps | 6.5 fps | 6.5 fps
|  |  | >4,400 Operating Hours per Year, Variable Flow/Variable Speed | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 110 gpm | 110 gpm | 110 gpm
|  |  | 3" | 170 gpm | 170 gpm | 170 gpm
|  |  | 4" | 320 gpm | 320 gpm | 320 gpm
|  |  | 5" | 370 gpm | 370 gpm | 370 gpm
|  |  | 6" | 680 gpm | 680 gpm | 680 gpm
|  |  | 8" | 1100 gpm | 1100 gpm | 1100 gpm
|  |  | 10" | 1600 gpm | 1600 gpm | 1600 gpm
|  |  | 12" | 2300 gpm | 2300 gpm | 2300 gpm
|  |  | >12" | 7.5 fps | 7.5 fps | 7.5 fps
|  |  | >4,400 Operating Hours per Year, Other | Maximum design flow | Maximum design flow | Maximum design flow
|  |  | 2.5" | 68 gpm | 68 gpm | 68 gpm
|  |  | 3" | 110 gpm | 110 gpm | 110 gpm
|  |  | 4" | 210 gpm | 210 gpm | 210 gpm
|  |  | 5" | 250 gpm | 250 gpm | 250 gpm
|  |  | 6" | 440 gpm | 440 gpm | 440 gpm
|  |  | 8" | 700 gpm | 700 gpm | 700 gpm
|  |  | 10" | 1000 gpm | 1000 gpm | 1000 gpm
|  |  | 12" | 1500 gpm | 1500 gpm | 1500 gpm
|  |  | >12" | 5.0 fps | 5.0 fps | 5.0 fps
|  | Chilled-Water Coil Selection |  |  |  | ≥15° Temperature Differential
≥57° Leaving water temperature @ design conditions
Heat Rejection Equipment
|  |  | Fan Speed Control | ≥7.5 hp | Each fan ≥7.5 hp | Individual motor or
array of motors ≥5 hp
|  |  | Multiple-cell equipment with variable speed fans |  | Operate maximum number of fans that comply with manufacturer's requirements for all components | Operate maximum number of fans that comply with manufacturer's requirements for all components
[5 empty] | Operate all fans at same speed | Operate all fans at same speed
|  |  | Limitation on centrifugal fan open-circuit cooling towers |  | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers | Towers with combined rated capacity ≥1,100 gpm at 95°F condenser water return, 85°F condenser water supply and 75°F outdoor wb temperature shall meet energy efficiency requirements for axial fan open-circuit cooling towers
|  |  | Tower fan turndown |  | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell | Open-circuit towers configured with multiple- or variable-speed condenser water pumps designed so that all cells run in parallel with the larger of flow that is produced by smallest pump at minimum expected flow rate or at 50% of design flow for the cell
Energy Recovery
|  |  | Exhaust Air Energy Recovery | 50% Energy Recovery Efficiency For Each Fan System Based on Outdoor Air Percentage of Full Design Flow (Exception: Where Largest Exhaust Air at Single Location < 75% of Design Outdoor Air Flow Rate) | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air | Provide change in outdoor air enthalpy ≥50% difference between outdoor air and return air
[5 empty] | For each fan system based on outdoor air percentage of full design flow (Exception: where largest exhaust air at single location < 75% of design outdoor air flow rate) | For each fan system based on outdoor air percentage of full design flow (Exception: where sum of exhaust air within 20 ft of each other < 75% of design outdoor air flow rate with some exclusions)
[5 empty] | Provisions to bypass or control energy recovery system to permit air economizer operation | Provisions to bypass or control energy recovery system to permit air economizer operation
|  |  | Energy Recovery Requirements - % Outdoor Air at Full Design Airflow Rate |  | Required for Systems with Design Supply Fan Flow Rate | Required for Systems with Design Supply Fan Flow Rate
[5 empty] | On systems operating <8,000 hours per year | On systems operating <8,000 hours per year
|  |  | ≥10% & <20% |  | ≥26,000 cfm | ≥26,000 cfm
|  |  | ≥20% & <30% |  | ≥16,000 cfm | ≥16,000 cfm
|  |  | ≥30% & <40% | ≥5,500 cfm | ≥5,500 cfm | ≥5,500 cfm
|  |  | ≥40% & <50% | ≥4,500 cfm | ≥4,500 cfm | ≥4,500 cfm
|  |  | ≥50% & <60% | ≥3,500 cfm | ≥3,500 cfm | ≥3,500 cfm
|  |  | ≥60% & <70% | ≥2,000 cfm | ≥2,000 cfm | ≥2,000 cfm
|  |  | ≥70% & <80% | ≥1,000 cfm | ≥1,000 cfm | ≥1,000 cfm
|  |  | ≥80% | ≥0 cfm | ≥0 cfm | ≥120 cfm
[5 empty] | On systems operating ≥8,000 hours per year | On systems operating ≥8,000 hours per year
|  |  | ≥10% & <20% |  |  | ≥200 cfm
|  |  | ≥20% & <30% |  |  | ≥130 cfm
|  |  | ≥30% & <40% | ≥5,500 cfm | ≥0 cfm | ≥100 cfm
|  |  | ≥40% & <50% | ≥4,500 cfm | ≥0 cfm | ≥80 cfm
|  |  | ≥50% & <60% | ≥3,500 cfm | ≥0 cfm | ≥70 cfm
|  |  | ≥60% & <70% | ≥2,000 cfm | ≥0 cfm | ≥60 cfm
|  |  | ≥70% & <80% | ≥1,000 cfm | ≥0 cfm | ≥50 cfm
|  |  | ≥80% | ≥0 cfm | ≥0 cfm | ≥40 cfm
|  |  | Heat Recovery for Service Water Heating | Required for 24 Hours a Day Operation, with >6,000,000 Btu/h Heat Rejection Capacity and >1,000,000 Btu/h Design Service Water Heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load | Required for 24 hours a day operation, with >6,000,000 Btu/h heat rejection capacity and >1,000,000 Btu/h design service water heating Load
[5 empty] | Capacity to provide smaller of | Capacity to provide smaller of
[5 empty] | 1) 60% peak heat rejection load at design conditions | 1) 60% peak heat rejection load at design conditions
[5 empty] | 2) Preheating required to raise peak service hot water draw to 85°F | 2) Preheating required to raise peak service hot water draw to 85°F
Exhaust Systems
|  |  | Transfer Air |  |  | Supply air shall not exceed the greater of
Flow required to meet space heating or cooling load
Required ventilation rate
Exhaust flow minus available transfer air on same floor
|  |  | Kitchen exhaust systems | Replacement Air Directly into Hood Cavity ≤10% of Hood Airflow Rate | Replacement air directly into hood cavity ≤10% of hood airflow rate | Replacement air directly into hood cavity ≤10% of hood airflow rate
|  |  |  | Conditioned Supply Air Delivered to Kitchen Hood Space Limitations | Conditioned supply air delivered to kitchen hood flow limitations | Conditioned supply air delivered to kitchen hood flow limitations
|  |  |  | For Total Hood Exhaust Rate >5,000 cfm: Each Hood Has Exhaust Rate Limitations and System Has Design Criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria | For total hood exhaust rate >5,000 cfm: each hood has exhaust rate limitations and system has design criteria
|  |  |  | Performance Testing Required | Performance testing required | Performance testing required
|  |  | Fume (laboratory) hood systems that use exception for energy recovery | Variable Exhaust & Supply Systems or Heat Recovery System for Systems >5,000 cfm Total Exhaust | Variable exhaust & supply systems or heat recovery system for systems >5,000 cfm total exhaust | Variable exhaust & supply systems or heat recovery system for systems >5,000 cfm total exhaust
Radiant Heating Systems
|  |  | For Unenclosed Spaces | Required | Required and controlled when required | Required and controlled when required
|  |  | For Enclosed Spaces | Conform with Governing Standards | Conform with governing standards | Conform with governing standards
| Hot Gas Bypass Limitation |  |  | Systems With Multiple Steps of Unloading | Systems with Multiple Steps of Unloading or Continuous Capacity Modulation | Systems with Multiple Steps of Unloading or Continuous Capacity Modulation
|  |  | ≤240,000 Btu/h Rated Capacity | ≤50% Maximum Bypass Capacity | ≤15% maximum bypass capacity | ≤15% maximum bypass capacity
|  |  | >240,000 Btu/h Rated Capacity | ≤25% Maximum Bypass Capacity | ≤10% maximum bypass capacity | ≤10% maximum bypass capacity
Door Switches
|  |  | Any conditioned space with door, including doors with >50% glass, opening to outdoors |  | Doors provided with controls, that when door is open: | Doors provided with controls, that when door is open:
[5 empty] | Disable mechanical heating or reset heating setpoint to ≤55° within 5 minutes of door opening | Disable mechanical heating or reset heating setpoint to ≤55° within 5 minutes of door opening
[5 empty] | Disable mechanical cooling or reset cooling setpoint to ≥90° within 5 minutes of door opening. | Disable mechanical cooling or reset cooling setpoint to ≥90° within 5 minutes of door opening.
[5 empty] | Mechanical cooling may remain enabled if outdoor air temperature < space temperature | Mechanical cooling may remain enabled if outdoor air temperature < space temperature
[5 empty] | Exceptions: | Exceptions:
[5 empty] | Building entries with automatic closing devices | Building entries with automatic closing devices
[5 empty] | Space without thermostat | Space without thermostat
[5 empty] | Alterations to existing buildings | Alterations to existing buildings
[5 empty] | Loading docks | Loading docks
Refrigeration Equipment Performance
|  | Commercial refrigeration, holding temperature application |  |  | Energy use limits (kWh per day) | Energy use limits (kWh per day)
|  |  | Refrigerator with solid doors |  | 0.10 x V + 2.04 | 0.10 x V + 2.04
|  |  | Refrigerator with transparent doors |  | 0.12 x V + 3.34 | 0.12 x V + 3.34
|  |  | Freezers with solid doors |  | 0.40 x V + 1.38 | 0.40 x V + 1.38
|  |  | Freezers with transparent doors |  | 0.75 x V + 4.10 | 0.75 x V + 4.10
|  |  | Refrigerators/freezers with solid doors |  | Greater of 0.12 x V + 3.34 or 0.70 | Greater of 0.12 x V + 3.34 or 0.70
|  | Commercial refrigeration, pulldown application |  |  | Energy use limits (kWh per day) | Energy use limits (kWh per day)
|  |  | Commercial refrigerators |  | 0.126 x V +3.51 | 0.126 x V +3.51
|  | Commercial refrigerators and freezers, remote condensing |  |  | Minimum Efficiency | Minimum Efficiency
|  |  | Vertical open, medium temp |  | 0.82 x TDA + 4.07 | 0.82 x TDA + 4.07
|  |  | Semivertical open, medium temp |  | 0.83 x TDA + 3.18 | 0.83 x TDA + 3.18
|  |  | Horizontal open, medium temp |  | 0.35 x TDA + 2.88 | 0.35 x TDA + 2.88
|  |  | Vertical open, low temp |  | 2.27 x TDA + 6.85 | 2.27 x TDA + 6.85
|  |  | Horizontal open, low temp |  | 0.57 x TDA + 6.88 | 0.57 x TDA + 6.88
|  |  | Vertical transparent door, medium temp |  | 0.22 x TDA + 1.95 | 0.22 x TDA + 1.95
|  |  | Vertical transparent door, low temp |  | 0.56 x TDA + 2.61 | 0.56 x TDA + 2.61
|  |  | Service over counter, medium temp |  | 0.51 x TDA + 0.11 | 0.51 x TDA + 0.11
|  | Commercial refrigerators and freezers, self-contained |  |  | Minimum Efficiency | Minimum Efficiency
|  |  | Vertical open, medium temp |  | 1.74 x TDA + 4.71 | 1.74 x TDA + 4.71
|  |  | Semivertical open, medium temp |  | 1.73 x TDA + 4.59 | 1.73 x TDA + 4.59
|  |  | Horizontal open, medium temp |  | 0.77 x TDA + 5.55 | 0.77 x TDA + 5.55
|  |  | Horizontal open, low temp |  | 1.92 x TDA + 7.08 | 1.92 x TDA + 7.08
|  |  | Vertical transparent door, ice cream temp |  | 0.67 x TDA + 3.29 | 0.67 x TDA + 3.29
|  |  | Vertical solid door, ice cream temp |  | 0.38 x V +0.88 | 0.38 x V +0.88
|  |  | Horizontal transparent door, ice cream temp |  | 0.56 x TDA + 0.43 | 0.56 x TDA + 0.43
|  | Commercial refrigerators and freezers, remote condensing |  |  | Minimum Efficiency | Minimum Efficiency
|  |  | Semivertical open, low temp |  | 2.27 x TDA + 6.85 | 2.27 x TDA + 6.85
|  |  | Vertical open, ice cream temp |  | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7
|  |  | Semivertical open, ice cream temp |  | 2.89 x TDA + 8.7 | 2.89 x TDA + 8.7
|  |  | Horizontal open, ice cream temp |  | 0.72 x TDA + 8.74 | 0.72 x TDA + 8.74
|  |  | Vertical transparent door, ice cream temp |  | 0.66 x TDA + 3.05 | 0.66 x TDA + 3.05
|  |  | Horizontal transparent door, medium temp |  | 0.16 x TDA + 0.13 | 0.16 x TDA + 0.13
|  |  | Horizontal transparent door, low temp |  | 0.34 x TDA + 0.26 | 0.34 x TDA + 0.26
|  |  | Horizontal transparent door, ice cream temp |  | 0.4 x TDA + 0.31 | 0.4 x TDA + 0.31
|  |  | Vertical solid door, medium temp |  | 0.11 x V + 0.26 | 0.11 x V + 0.26
|  |  | Vertical solid door, low temp |  | 0.23 x V + 0.54 | 0.23 x V + 0.54
|  |  | Vertical solid door, ice cream temp |  | 0.27 x V + 0.63 | 0.27 x V + 0.63
|  |  | Horizontal solid door, medium temp |  | 0.11 x V + 0.26 | 0.11 x V + 0.26
|  |  | Horizontal solid door, low temp |  | 0.23 x V + 0.54 | 0.23 x V + 0.54
|  |  | Horizontal solid door, ice cream temp |  | 0.27 x V + 0.63 | 0.27 x V + 0.63
|  |  | Service over counter, low temp |  | 1.08 x TDA + 0.22 | 1.08 x TDA + 0.22
|  |  | Service over counter, ice cream temp |  | 1.26 x TDA + 0.26 | 1.26 x TDA + 0.26
|  | Commercial refrigerators and freezers, self-contained |  |  | Minimum Efficiency | Minimum Efficiency
|  |  | Vertical open, low temp |  | 4.37 x TDA + 11.82 | 4.37 x TDA + 11.82
|  |  | Vertical open, ice cream temp |  | 5.55 x TDA + 15.02 | 5.55 x TDA + 15.02
|  |  | Semivertical open, low temp |  | 4.34 x TDA + 11.51 | 4.34 x TDA + 11.51
|  |  | Semivertical open, ice cream temp |  | 5.52 x TDA + 14.63 | 5.52 x TDA + 14.63
|  |  | Horizontal open, ice cream temp |  | 2.44 x TDA + 9.0 | 2.44 x TDA + 9.0
|  |  | Service over counter, ice cream temp |  | 1.76 x TDA + 0.36 | 1.76 x TDA + 0.36
|  |  | Horizontal solid door, ice cream temp |  | 0.38 x V + 0.88 | 0.38 x V + 0.88
Walk-in Coolers and Walk-in Freezers that are Site Assembled or Site Constructed
|  |  | Door-closers |  | Automatic within 1" of full closure | Automatic within 1" of full closure
|  |  | Doorway infiltration control |  | Strip door curtains, spring hinged doors or other method | Strip door curtains, spring hinged doors or other method
|  |  | Insulation for walk-in coolers |  | ≥R-25 for walls | ≥R-25 for walls
[5 empty] | ≥R-25 for ceiling | ≥R-25 for ceiling
[5 empty] | ≥R-25 for cooler doors | ≥R-25 for cooler doors
|  |  | Insulation for walk-in freezers |  | ≥R-32 for walls | ≥R-32 for walls
[5 empty] | ≥R-32 for ceiling | ≥R-32 for ceiling
[5 empty] | ≥R-32 for freezer doors | ≥R-32 for freezer doors
[5 empty] | ≥R-28 for freezer floor | ≥R-28 for freezer floor
|  |  | Transparent reach-in doors for walk-in freezers & windows in opaque walk-in freezer doors |  | Triple-pane glass, either filled with inert gas or heat-reflective treated glass | Triple-pane glass, either filled with inert gas or heat-reflective treated glass
|  |  | Transparent reach-in doors for walk-in coolers & windows in opaque doors for walk-in coolers |  | Double-pane, inert gas-filled, heat-reflective treated glass, or triple-pane glass with inert gas or heat-reflective treated glass | Double-pane, inert gas-filled, heat-reflective treated glass, or triple-pane glass with inert gas or heat-reflective treated glass
|  |  | Evaporative fan motors <1 hp and <460 v |  | Electronically commutated motors (brushless direct-current motors) or 3-phase motors | Electronically commutated motors (brushless direct-current motors) or 3-phase motors
|  |  | Condenser fan motors <1 hp |  | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors | Electronically commutated motors or, permanent split capacitor-type motors or 3- phase motors
|  |  | Antisweat heaters without antisweat heater controls (total door rail, glass and frame heater power draw) |  | ≤7.1 W/sf of door opening for walk-in freezers | ≤7.1 W/sf of door opening for walk-in freezers
[5 empty] | ≤3.0 W/sf of door opening for walk-in coolers | ≤3.0 W/sf of door opening for walk-in coolers
|  |  | Antisweat heater control |  | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or condensation on inner glass pane
|  |  | Lights |  | Efficacy ≥40 lumens per watt, including ballast losses or | Efficacy ≥40 lumens per watt, including ballast losses or
[5 empty] | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy | Efficacy <40 lumens per watt, including ballast losses, in conjunction with device that automatically turns off lights within 15 minutes after occupancy
|  |  | Walk-in freezer temperature based defrost termination control |  | First on upper temperature limit breach, second upon time limit breach | First on upper temperature limit breach, second upon time limit breach
Refrigerated Display Cases, Site Assembled or Site Constructed
|  |  | Lighting control |  | Time switch to turn lights off during nonbusiness hours or | Time switch to turn lights off during nonbusiness hours or
[5 empty] | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated | Motion sensor control on each section that reduces lighting power ≥50% within 3 minutes after area is vacated
|  |  | Low-temperature display cases |  | Temperature-based defrost termination control with time-limit default | Temperature-based defrost termination control with time-limit default
|  |  | Antisweat heater controls |  | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane | Reduce energy use as function of relative humidity in air outside the door or to condensation on inner glass pane
Refrigeration Systems
Refrigerated display cases, walk-in coolers or walk-in freezers served by remote compressors and remote condensers not located in a condensing unit (exception for working fluid that goes through both subcritical and super critical states or that uses ammonia refrigerant)
|  |  | Fan-powered condensers |  | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 10°F for low temperature systems
[5 empty] | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems | Design saturated condensing temperature for air cooled condensers ≤ design db temperature plus 15°F for medium temperature systems
[5 empty] | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors | Fan motors <1 hp shall be electronically commutated motors, permanent split-capacitor-type motors or 3-phase motors
[5 empty] | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control | Capability to reduce fan motor demand to ≤30% design wattage at 50% design air volume and incorporate continuous variable speed fan control
[5 empty] | Multiple fan condensers controlled in unison | Multiple fan condensers controlled in unison
[5 empty] | Minimum condensing temperature setpoint ≤70°F | Minimum condensing temperature setpoint ≤70°F
|  |  | Compressor systems |  | Floating suction pressure control on compressors & multiple-compressor system suction groups | Floating suction pressure control on compressors & multiple-compressor system suction groups
[5 empty] | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity | Liquid subcooling on all low-temperature compressor systems ≥100,000 Btu/h cooling capacity
[5 empty] | Crankcase heaters cycled off during compressor operation | Crankcase heaters cycled off during compressor operation
Alternate Compliance Path
|  | Computer room systems |  |  | HVAC systems serving heating, cooling or ventilating needs of computer room may comply with: | HVAC systems serving heating, cooling or ventilating needs of computer room may comply with:
[5 empty] | Computer room PUE1 ≤1.36 | Computer room PUE1 ≤1.36
[5 empty] | Highest value computer room PUE0 ≤1.36 where PEU0 calculated at 100% design IT equipment energy use and 50% design IT equipment energy | Highest value computer room PUE0 ≤1.36 where PEU0 calculated at 100% design IT equipment energy use and 50% design IT equipment energy
[5 empty] | Provide documentation | Provide documentation
HVAC Completion Requirements
Record Drawings
|  |  | Record Drawings of Actual Installation Including Performance Data Provided to Owner | Construction documents to require submittal within 90 days of system acceptance | Construction documents to require submittal within 90 days of system acceptance | Construction documents to require submittal within 90 days of system acceptance
Manuals
|  |  | Operating Manual | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-1993) | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-2008) | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-2008)
|  |  | Maintenance Manual | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-1993) | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-2008) | Construction documents to require submittal within 90 days of system acceptance (Guideline 4-2008)
System Balancing
|  |  | Report Provided to Owner | To Be Required by Construction Documents for Systems Serving Zones with Total Conditioned Area >5,000 sq. ft. | Written report for HVAC systems serving zones with total conditioned area >5,000 sf | Written report for HVAC systems serving zones with total conditioned area >5,000 sf
System Commissioning
|  |  | HVAC Control Systems Tested to Ensure Calibration, Adjustment and Working Condition | To Be Required by Construction Documents for Projects with Conditioned Area >50,000 sq. ft. (Guideline 1-1996) | To Be Required by Construction Documents for Projects with Conditioned Area >50,000 sq. ft. (Guideline 1.1-2007) | To Be Required by Construction Documents for Projects with Conditioned Area >50,000 sq. ft. (Guideline 1.1-2007)
Service Water Heating
Equipment Efficiency
High input-rated service water-heating-systems
[5 empty] | Gas-fired water heater in new building | Gas-fired water heater in new building
|  |  | Singular piece serving entire building, rated ≥1,000,000 Btu/h |  | ≥90% Et | ≥90% Et
|  |  | Multiple pieces serving building, combined rated input ≥1,000,000 Btu/h |  | ≥90% Et, combined input-capacity-weighted-average | ≥90% Et, combined input-capacity-weighted-average
Electric Table Top Water Heaters
|  |  | ≤12 kW, Resistance, ≥20 gal | 0.93 - 0.00132V EF | 0.93 - 0.00035V EF | per 10 CFR Prt 430
Electric Water Heaters
|  |  | ≤12 kW, Resistance, ≥20 gal | 0.97 - 0.00132V EF | 0.97 - 0.00035V EF | per 10 CFR Prt 430
|  |  | >12 kW, Resistance, ≥20 gal | 20 + 35√V SL, Btu/h | (0.3 + 27/Vm), %/h | (0.3 + 27/Vm), %/h
|  |  | ≤24 Amps and ≤250 Volts, Heat Pump | 0.93 - 0.00132V EF | 0.93 - 0.00035V EF | per 10 CFR Prt 430
Gas Storage Water Heaters
|  |  | ≤75,000 Btu/h, ≥20 gal | 0.67 - 0.0019V EF | 0.67 - 0.0005V EF | per 10 CFR Prt 430
|  |  | >75000 Btu/h, < 4000 (Btu/h)/gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/799 + 16.6√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Gas Instantaneous Water Heaters
|  |  | >50,000 and <200,000 Btu/h, ≥4,000 (Btu/h)/gal and <2 gal | 0.62 - 0.0019V EF | 0.62 - 0.0005V EF | per 10 CFR Prt 430
|  |  | ≥200,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
|  |  | >200,000 Btu/h, ≥4,000 (Btu/h)/gal and ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/799 + 16.6√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Oil Storage Water Heaters
|  |  | ≤105,000 Btu/h, ≥20 gal | 0.59 - 0.0019V EF | 0.59 - 0.0005V EF | per 10 CFR Prt 430
|  |  | >105,000 Btu/h, <4,000 (Btu/h)/gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/799 + 16.6√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Oil Instantaneous Water Heaters
|  |  | ≤210,000 Btu/h, ≥4,000 (Btu/h)/gal and <2 gal | 0.59 - 0.0019V EF | 0.59 - 0.0005V EF | per 10 CFR Prt 430
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
|  |  | >210,000 Btu/h, ≥4,000 (Btu/h)/gal and ≥10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/799 + 16.6√V) SL, Btu/h | 78% Et (Q/800 + 110√V) SL, Btu/h
Hot Water Supply Boilers, Gas and Oil
|  |  | ≥300,000 and <12,500,000 Btu/h, ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | 80% Et | 80% Et
Hot Water Supply Boilers, Gas
|  |  | ≥4,000 (Btu/h)/gal and ≥10 gal | 80% Et (Q/800 + 110√V) SL, Btu/h | 80% Et (Q/799 + 16.6√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
Hot Water Supply Boilers, Oil
|  |  | ≥4,000 (Btu/h)/gal and ≥10 gal | 78% Et (Q/800 + 110√V) SL, Btu/h | 78% Et (Q/799 + 16.6√V) SL, Btu/h | 80% Et (Q/800 + 110√V) SL, Btu/h
| Pool Heaters, Oil and Gas |  |  | 78% Et | 78% Et | per 10 CFR Prt 430
| Heat Pump Pool Heaters |  |  | 4.0 COP | 4.0 COP | 4.0 COP
| Unfired Storage Tanks |  |  | R-12.5 | R-12.5 | R-12.5
Service Hot Water Piping Insulation
|  | 105+ºF Fluid Temperature & 0.22 - 0.28 Insulation Conductivity |  | For Defined Locations | In mechanical system table | In mechanical system table
|  |  | <1" Nominal Pipe or Tube Size | 1.0"
|  |  | 1" to <1.5" Nominal Pipe or Tube Size | 1.0"
|  |  | 1.5" to <4"" Nominal Pipe or Tube Size | 1.5"
|  |  | 4" to <8" Nominal Pipe or Tube Size | 1.5"
|  |  | ≥8" Nominal Pipe or Tube Size | 1.5"
|  |  | Insulation Locations | Recirculating System Piping | Recirculating System Piping | Recirculating System Piping
|  |  |  | First 8 ft of outlet piping for constant temperature nonrecirculating storage system | First 8 ft of outlet piping for constant temperature nonrecirculating storage system | First 8 ft of outlet piping for constant temperature nonrecirculating storage system
|  |  |  | Inlet piping between storage ank & heat trap in nonrecirculating storage system | Inlet piping between storage ank & heat trap in nonrecirculating storage system | Inlet piping between storage ank & heat trap in nonrecirculating storage system
|  |  |  | Externally heated piping | Externally heated piping | Externally heated piping
Service Water Heating System Controls
|  |  | Storage Temperature Controls | ≤120ºF to Temperature Compatible with Intended Use | Setpoint ≤120ºF or temperature compatible with intended use | Setpoint ≤120ºF or temperature compatible with intended use
|  |  | Temperature Maintenance Controls in Hot Water Pipes | Automatic Time Switches/Controls for Extended Periods when Hot Water Not Required | Automatic Time Switches/Controls for Extended Periods when Hot Water Not Required | Automatic Time Switches/Controls for Extended Periods when Hot Water Not Required
|  |  | Outlet Temperature Controls for Lavatory Faucets in Public Restrooms | Delivered ≤110ºF | Delivered ≤110ºF | Delivered ≤110ºF
|  |  | Circulating Pump Controls for Storage Tanks | Limit Operation to Heating Cycle | Limit operation to ≤5 minutes after heating cycle | Limit operation to ≤5 minutes after heating cycle
Pools
|  | Pool Heaters |  | Readily Accessible On-Off Switch Without Adjusting Setpoint | Readily accessible on-off switch without adjusting setpoint | Readily accessible on-off switch without adjusting setpoint
Pool Covers
|  |  | Water Temperature ≤90ºF | Vapor Retardant Cover Required | Vapor retardant cover required | Vapor retardant cover required
|  |  | Water Temperature >90ºF | ≥R-12 | Vapor retardant cover required with ≥R-12 insulation | Vapor retardant cover required with ≥R-12 insulation
|  | Time Switches |  | Installed on Heaters and Pumps | Installed on swimming pool heaters and pumps | Installed on swimming pool heaters and pumps
Heat Traps
|  |  | Vertical Risers Serving Storage Water Heaters and Storage Tanks | Required on Both Inlet and Outlet Piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping | Supplied internal heat traps or provided with heat traps on supply and discharge piping
Combined Use
|  |  | Space Heating and Water Heating | Allowed with Conditions | Allowed with conditions | Allowed with conditions
|  |  | Service Water Heating Equipment | Allowed to Provide Space Heating if All Service Water Heating Equipment Requirements Are Met | Allowed to provide space heating if all service water heating equipment requirements are met | Allowed to provide space heating if all service water heating equipment requirements are met
Power
Mandatory Provisions
|  |  | Feeder Voltage Drop | ≤2% at Design Load | ≤2% at Design Load
|  |  | Branch Circuit Voltage Drop | ≤3% at Design Load | ≤3% at Design Load
|  |  | Combined Feeder & Branch Circuit Voltage Drop |  |  | ≤5% Total
|  |  | Automatic Receptacle Control | On ≥50% All 125v 15- & 20-Ampere Receptacles in | On ≥50% All 125v 15- & 20-Ampere Receptacles in | On ≥50% All 125v 15- & 20-Ampere Receptacles in
|  |  |  | Private offices | Private offices | Private offices
|  |  |  | Open offices | Conference rooms | Conference rooms
|  |  |  | Computer classrooms | Rooms used primarily for printing and/or copyig functions | Rooms used primarily for printing and/or copyig functions
[5 empty] | Breakrooms | Breakrooms
[5 empty] | Classrooms | Classrooms
[5 empty] | Individual workstations | Individual workstations
[5 empty] | On ≥25% branch feedder circuits for modular furniture not shown on construction documents | On ≥25% branch feedder circuits for modular furniture not shown on construction documents
[5 empty] | Control function based on | Control function based on
[5 empty] | Schedule | Schedule
[5 empty] | Occupant sensor | Occupant sensor
[5 empty] | Other control or alarm system | Other control or alarm system
[5 empty] | Permanently marked control receptacles | Permanently marked control receptacles
[5 empty] | Uniformly distributed throughout space | Uniformly distributed throughout space
[5 empty] | Plug-in devices not used for compliance | Plug-in devices not used for compliance
Electrical energy monitoring
|  |  | Applicability |  | New buildings | New buildings
[5 empty] | Exceptions: | Exceptions:
[5 empty] | Buildings <25,000 sf | Buildings <25,000 sf
[5 empty] | Individual tenant spaces <10,000 sf | Individual tenant spaces <10,000 sf
[5 empty] | Dwelling units | Dwelling units
[5 empty] | Residential buildings with <10,000 sf of common area | Residential buildings with <10,000 sf of common area
[5 empty] | Critical and equipment branches of NEC Article 517 | Critical and equipment branches of NEC Article 517
|  |  | Separately monitored area |  | Total building | Total building
[5 empty] | Each individual tenant space, excluding shared systems | Each individual tenant space, excluding shared systems
|  |  | Separately monitored energy use |  | Total electrical energy | Total electrical energy
[5 empty] | HVAC systems | HVAC systems
[5 empty] | Interior lighting | Interior lighting
[5 empty] | Exterior lighting | Exterior lighting
[5 empty] | Receptacle circuits | Receptacle circuits
|  |  | Recording and reporting |  | Recorded minimum of every 15 minutes | Recorded minimum of every 15 minutes
[5 empty] | Reported at least hourly, daily, monthly and annually | Reported at least hourly, daily, monthly and annually
[5 empty] | Store data for ≥36 months | Store data for ≥36 months
Low Voltage Dry-Type Distribution Transformers
|  |  | Single Phase (kVA) | Efficiency | Efficiency | Efficiency
|  |  | 15 | 97.7% | 97.7% | 97.7%
|  |  | 25 | 98% | 98% | 98%
|  |  | 37.5 | 98.2% | 98.2% | 98.2%
|  |  | 50 | 98.3% | 98.3% | 98.3%
|  |  | 75 | 98.5% | 98.5% | 98.5%
|  |  | 100 | 98.6% | 98.6% | 98.6%
|  |  | 167 | 98.7% | 98.7% | 98.7%
|  |  | 250 | 98.8% | 98.8% | 98.8%
|  |  | 333 | 98.9% | 98.9% | 98.9%
|  |  | Three Phase (kVA) |  | Efficiency | Efficiency
|  |  | 15 | 97% | 97% | 97.89%
|  |  | 30 | 97.5% | 97.5% | 98.23%
|  |  | 45 | 97.7% | 97.7% | 98.4%
|  |  | 75 | 98% | 98% | 98.6%
|  |  | 112.5 | 98.2% | 98.2% | 98.74%
|  |  | 150 | 98.3% | 98.3% | 98.83%
|  |  | 225 | 98.5% | 98.5% | 98.94%
|  |  | 300 | 98.6% | 98.6% | 99.02%
|  |  | 500 | 98.7% | 98.7% | 99.14%
|  |  | 750 | 98.8% | 98.8% | 99.23%
|  |  | 1000 | 98.9% | 98.9% | 99.28%
Completion Requirements
|  |  | Record Drawings of Actual Installation | Construction documents to require submittal within 30 days of system acceptance | Construction documents to require submittal within 30 days of system acceptance | Construction documents to require submittal within 30 days of system acceptance
|  |  | Operating Manual | Construction documents to require submittal | Construction documents to require submittal | Construction documents to require submittal
|  |  | Maintenance Manual | Construction documents to require submittal | Construction documents to require submittal | Construction documents to require submittal
Lighting
Alterations
|  |  | Alterations requiring compliance with lighting power density | Interior alterations involving ≥10% connected lighting load (including lamp plus ballast replacement) | Interior alterations involving ≥10% connected lighting load of space or area (including lamp plus ballast replacement) | Interior alterations involving >20% connected lighting load of space or area
Interior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
|  |  |  | Interior alterations involving <10% connected lighting load of space or area need not comply but can not increase installed lighting power | Interior alterations involving <10% connected lighting load of space or area need not comply but can not increase installed lighting power | Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
|  |  |  | Exterior alterations involving ≥10% connected lighting load (including lamp plus ballast replacement) | Exterior alterations involving ≥10% connected lighting load of space or area including luminaire additions, replacements and removal | Exterior alterations involving >20% connected lighting load of space or area
Exterior alterations involving ≤20% connected lighting load of space or area need NOT comply but can not increase installed lighting power
Exterior alterations involving lamp plus ballasts/drivers or one-for-one luminaire replacement
|  |  | Alterations requiring compliance with control requirements | Automatic shutoff control for interior alterations involving ≥10% connected lighting load (including lamp plus ballast replacement) | Automatic shutoff control for interior alterations involving ≥10% connected lighting load including luminaire additions, replacements and removal | Interior alterations involving >20% connected lighting load except for daylight controls
Interior alterations involving ≤20% connected lighting load of space or area need not comply but can not increase installed lighting power
Automatic/scheduled shutoff controls for interior lamp plus ballasts/drivers or one-for-one luminaire replacement
|  |  |  | Automatic shutoff for exterior alterations involving ≥10% connected lighting load including luminaire additions, replacements and removal | Automatic shutoff for exterior alterations involving ≥10% connected lighting load including luminaire additions, replacements and removal | Automatic shutoff & power reduction controls for exterior alterations involving >20% connected lighting load of space or area
Automatic/scheduled shutoff controls for exterior lamp plus ballasts/drivers or one-for-one luminaire replacement
Lighting Controls
Interior Lighting Controls
|  |  | Automatic Interior Lighting Shutoff Controls In All Spaces | All Buildings
|  |  | Any Automatc Control | Manual On or 50% automatic On Except In Public Corridors & Stairwells, Restrooms, Primary Entrance Areas & Lobbies, and Areas Where Manual-On Operation Would Endanger Safety or Security | All lighting (except emergency lighting that is automatically off during normal operation) automatically off during scheduled unoccupied periods (h)(i) | All lighting (except emergency lighting that is automatically off during normal operation) automatically off during scheduled unoccupied periods (h)(i)
[5 empty] | Scheduled OFF | Scheduled OFF
[5 empty] | Controlled by: | Controlled by:
[5 empty] | Time-of-day device | Time-of-day device
[5 empty] | Signal from another automatic control or alarm/security system | Signal from another automatic control or alarm/security system
|  |  | Control device for each interior enclosed space (area) | Occupancy Sensor or Time Switch Required in | All lighting control functions indicated in Table 9.6.1 | All lighting control functions indicated in Table 9.6.1
|  |  |  | Classrooms & Lecture Halls | Functions labeled "REQ" are mandatory | Functions labeled "REQ" are mandatory
|  |  |  | Conference,Meeting & Training Rooms | 1) If space type labeled "ADD1", ≥1 of those functions implemented in space | 1) If space type labeled "ADD1", ≥1 of those functions implemented in space
|  |  |  | Employee Lunch & Break Rooms | 2) If space type labeled "ADD2", ≥1 of those functions implemented in space | 2) If space type labeled "ADD2", ≥1 of those functions implemented in space
|  |  |  | Storage & Supply Rooms between 50 and 1000 sq. ft. | Functions: | Functions:
|  |  |  | Copying & Printing Rooms | Local control: ≥1 manual lighting controls in the space | Local control: ≥1 manual lighting controls in the space
|  |  |  | Office Space <250 sq. ft. | Restricted to manual ON | Restricted to manual ON
|  |  |  | Restrooms | Restricted to partial automatic ON | Restricted to partial automatic ON
|  |  |  | Dressing, Locker & Fitting Rooms | Bilevel lighting control | Bilevel lighting control
[5 empty] | Automatic daylight responsive controls for sidelighting | Automatic daylight responsive controls for sidelighting
[5 empty] | Automatic daylight responsive controls for toplighting | Automatic daylight responsive controls for toplighting
[5 empty] | Automatic partial OFF (full OFF complies) | Automatic partial OFF (full OFF complies)
[5 empty] | Automatic full OFF | Automatic full OFF
[5 empty] | Scheduled shutoff | Scheduled shutoff
|  |  | Light-reduction controls |  | Bilevel lighting control: Step between full ON and full OFF to be between 30% & 70% of full lighting power | Bilevel lighting control: Step between full ON and full OFF to be between 30% & 70% of full lighting power
|  |  | Manual controls |  | Readily accessible and located where the controlled lights are | Readily accessible and located where the controlled lights are
|  |  | Control Device for Each Interior Enclosed Space | At least One to Independently Control General Lighting | Control function per Table 9.6.1 | Control function per Table 9.6.1
[5 empty] | Restricted to manual ON | Restricted to manual ON
|  |  |  | 0%, 30-70%, 100% Control Steps | Restricted to partial ON: ≤50% automatically turn on and remainder to be manually turned on | Restricted to partial ON: ≤50% automatically turn on and remainder to be manually turned on
|  |  |  | Manual On or Occupancy Sensor Controls In Other Spaces ≤2,500 sq. ft. for Space ≤10,000 sq. ft. and ≤10,000 sq. ft. for Space >10,000 sq. ft. | Automatic partial OFF (full OFF complies): automatically reduces lighting by ≥50% within 20 minutes of occupants leaving | Automatic partial OFF (full OFF complies): automatically reduces lighting by ≥50% within 20 minutes of occupants leaving
[5 empty] | Automatic full OFF within 20 minutes of occupants leaving | Automatic full OFF within 20 minutes of occupants leaving
|  |  | Daylight responsive controls | For Combined Primary Sidelighted Area in Enclosed Space ≥250 sq. ft. | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within primary sidelight daylight zone | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within primary sidelight daylight zone
|  |  |  | General Lighting in Primary Sidelighted Area Controlled Separately | Photocontrol lighting in spaces with ≥300 watts of general lighting completely or partially within primary and secondary sidelight daylight zone | Photocontrol lighting in spaces with ≥300 watts of general lighting completely or partially within primary and secondary sidelight daylight zone
|  |  |  | Automatic Multilevel Photocontrol with One Step Between 50-70% and Another Step <35% (Including Off) of Design Power | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within daylight areas under skylights & roof monitors | Photocontrol lighting in spaces with ≥150 watts of general lighting completely or partially within daylight areas under skylights & roof monitors
For Total Daylight Area Under Skylights in Enclosed Space ≥900 sq.ft.
General Lighting In Daylight Area Controlled Separately
Automatic Multilevel Photocontrol with One Step Between 50-70% and Another Step <35% (Including Off) of Design Power
|  |  | Daylight-responsive control functions (Daylight zone control) |  | General lighting in secondary sidelighted area controlled independently of primary sidelight area | General lighting in secondary sidelighted area controlled independently of primary sidelight area
[5 empty] | General lighting in overlapping toplighted and sidelighted daylight areas controlled together | General lighting in overlapping toplighted and sidelighted daylight areas controlled together
[5 empty] | Readily accessible calibration mechanism | Readily accessible calibration mechanism
[5 empty] | Photocontrol to reduce lighting by continuous dimming or with one control point between 50% & 70%, with second control point between 20% & 40% (or lowest dimming level the technology allows) and third control point is OFF | Photocontrol to reduce lighting by continuous dimming or with one control point between 50% & 70%, with second control point between 20% & 40% (or lowest dimming level the technology allows) and third control point is OFF
[5 empty] | Primary sidelight area | Primary sidelight area
[5 empty] | Directly adjacent to vertical fenestration | Directly adjacent to vertical fenestration
[5 empty] | Width is width of fenestration plus, on each side, the smaller of: | Width is width of fenestration plus, on each side, the smaller of:
[5 empty] | 1) ½ fenestration head height (floor to top of glazing) or | 1) ½ fenestration head height (floor to top of glazing) or
[5 empty] | 2) Distance to opaque vertical obstruction ≥5' high | 2) Distance to opaque vertical obstruction ≥5' high
[5 empty] | Depth is smaller of perpendicular distance from fenestration: | Depth is smaller of perpendicular distance from fenestration:
[5 empty] | 1) Vertical head height or | 1) Vertical head height or
[5 empty] | 2) Distance to opaque vertical obstruction ≥5' high | 2) Distance to opaque vertical obstruction ≥5' high
[5 empty] | Secondary sidelight area | Secondary sidelight area
[5 empty] | Directly adjacent to primary sidelight area | Directly adjacent to primary sidelight area
[5 empty] | Width is width of fenestration plus, on each side, the smaller of: | Width is width of fenestration plus, on each side, the smaller of:
[5 empty] | 1) ½ fenestration head height (floor to top of glazing) or | 1) ½ fenestration head height (floor to top of glazing) or
[5 empty] | 2) Distance to opaque vertical obstruction ≥5' high | 2) Distance to opaque vertical obstruction ≥5' high
[5 empty] | Depth is smaller of perpendicular distance from fenestration: | Depth is smaller of perpendicular distance from fenestration:
[5 empty] | 1) Vertical head height or | 1) Vertical head height or
[5 empty] | 2) Distance to opaque vertical obstruction ≥5' high | 2) Distance to opaque vertical obstruction ≥5' high
[5 empty] | Secondary sidelight area | Secondary sidelight area
[5 empty] | If primary sidelight area ends at opaque vertical obstruction ≥5' high, there is no secondary sidelight area | If primary sidelight area ends at opaque vertical obstruction ≥5' high, there is no secondary sidelight area
[5 empty] | Daylight area under roof monitor | Daylight area under roof monitor
[5 empty] | Width is width of fenestration plus, on each side, the smaller of: | Width is width of fenestration plus, on each side, the smaller of:
[5 empty] | 1) 2 ft or | 1) 2 ft or
[5 empty] | 2) Distance to opaque vertical obstruction ≥5' high or | 2) Distance to opaque vertical obstruction ≥5' high or
[5 empty] | 3) Distance to edge of any primary sidelighted area | 3) Distance to edge of any primary sidelighted area
[5 empty] | Depth is smaller inward distance from bottom edge of fenestration: | Depth is smaller inward distance from bottom edge of fenestration:
[5 empty] | 1) Montor sill height (floor to bottom edge of glazing) or | 1) Montor sill height (floor to bottom edge of glazing) or
[5 empty] | 2) Distance to nearest opaque vertical obstruction, where any part of obstruction is farther than the difference between height of obstruction and monitor sill height | 2) Distance to nearest opaque vertical obstruction, where any part of obstruction is farther than the difference between height of obstruction and monitor sill height
[5 empty] | Daylight area under skylight | Daylight area under skylight
[5 empty] | Area bounded by opening beneath skylight & horizontally in each direction, smaller of: | Area bounded by opening beneath skylight & horizontally in each direction, smaller of:
[5 empty] | a) 70% ceiling height or | a) 70% ceiling height or
[5 empty] | b) Distance to nearest opaque vertical obstruction where any part of obstruction is father than 70% distance between top of obstruction & ceiling at lowest edge of skylight | b) Distance to nearest opaque vertical obstruction where any part of obstruction is father than 70% distance between top of obstruction & ceiling at lowest edge of skylight
|  |  | Parking Garage Lighting Control | Automatic Lighting Shutoff | Automatic lighting shutoff | Automatic lighting shutoff
|  |  |  | Automatic ≥30% Reduction When No Activity ≤30 Minutes | Automatic ≥30% reduction when no activity ≤20 minutes | Automatic ≥30% reduction when no activity ≤20 minutes
|  |  |  | Daylight Transition Zone Separately Control, Automatically On During Daylight and Off at Sunset | ≥50% automatic reduction from sunset to sunrise on covered vehicle entrance & exit ramps | ≥50% automatic reduction from sunset to sunrise on covered vehicle entrance & exit ramps
|  |  |  | Photosensor Control Dimming Within 20' of Wall With ≥40% Window Wall Ratio | Photocontrol dimming within 20' of wall with ≥40% window wall ratio & no exterior obstructions | Photocontrol dimming within 20' of wall with ≥40% window wall ratio & no exterior obstructions
Exterior Lighting Control
|  |  |  | Automatic Shut-Off When Sufficient Daylight Available or Not Required | Automatic shut-off when sufficient daylight available | Automatic shut-off when sufficient daylight available
|  |  |  | Facade and Landscape Lighting Automatically Off Between Midnight or Business Closing and 6 am | Facade and landscape lighting automatically off between midnight or business closing and 6 am or business opening | Facade and landscape lighting automatically off between midnight or business closing and 6 am or business opening
|  |  |  | ≥30% Automatic Reduction In Connected Power For Other Lighting After Hours or No Activity | Other than façade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes | Other than façade or landscape lighting, configure controls to automatically reduce connected lighting power ≥30% from midnight to 6 am, from 1 hour after business closing to 1 hour before business opening or during any period when activity not detected for >15 minutes
Special Application
|  |  | Display/Accent Lighting | Separate Control Device | Separate control device | Separate control device
|  |  | Case Lighting | Separate Control Device | Separate control device | Separate control device
|  |  | Nonvisual Lighting | Separate Control Device | Separate control device | Separate control device
|  |  | Demonstration Lighting | Separate Control Device | Separate control device | Separate control device
|  |  | Hotel, Motel and Boarding House Guest Room and Guest Suite Lighting | Control Device(s) At Entry Door for Permanently Installed Luminaires and Switched Receptacles | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room | Control device capable of automatically switching off all installed luminaires and switched receptacles ≤20 minutes after occupants leave room
|  |  |  | Occupancy Sensor for Bathrooms | Separate occupant sensing control for bathrooms | Separate occupant sensing control for bathrooms
|  |  | Supplemental Task Lighting | Occupant Accessible Control Device (Must Have Automatic Shutoff Control To Be Exempt From Interior Lighting Power) | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power) | Control device integral to luminaires or controlled by readily accessible wall-mounted control device (must have automatic shutoff control to be exempt from connected interior lighting power)
|  |  | Stairwell Lighting | Automatic Control Device To Reduce Lighting Power ≥50% | Automatic Control Device To Reduce Lighting Power ≥50% | Automatic Control Device To Reduce Lighting Power ≥50%
| Exit Signs |  |  | ≤5 watts per Face for Internally Illuminated
Interior Lighting Power
|  | Building Area Method - Lighting Power Densities |  | w/sf | w/sf | w/sf
|  |  | Automotive Facility | 0.82 | 0.8 | 0.71
|  |  | Convention Center | 1.08 | 1.01 | 0.76
|  |  | Court House | 1.05 | 1.01 | 0.9
|  |  | Dining: Bar Lounge/Leisure | 0.99 | 1.01 | 0.9
|  |  | Dining: Cafeteria/Fast Food | 0.9 | 0.9 | 0.79
|  |  | Dining: Family | 0.89 | 0.95 | 0.78
|  |  | Dormitory | 0.61 | 0.57 | 0.61
|  |  | Exercise Center | 0.88 | 0.84 | 0.65
|  |  | Gymnasium | 1 | 0.94 | 0.68
|  |  | Healthcare - Clinic | 0.87 | 0.9 | 0.82
|  |  | Hospital | 1.21 | 1.05 | 1.05
|  |  | Hotel | 1 | 0.87 | 0.75
|  |  | Library | 1.18 | 1.19 | 0.78
|  |  | Manufacturing Facility | 1.11 | 1.17 | 0.9
|  |  | Motel | 0.88 | 0.87 | 0.75
|  |  | Motion Picture Theater | 0.83 | 0.76 | 0.83
|  |  | Multi-Family | 0.6 | 0.51 | 0.68
|  |  | Museum | 1.06 | 1.02 | 1.06
|  |  | Office | 0.9 | 0.82 | 0.79
|  |  | Parking Garage | 0.25 | 0.21 | 0.15
|  |  | Penitentiary | 0.97 | 0.81 | 0.75
|  |  | Performing Arts Theater | 1.39 | 1.39 | 1.18
|  |  | Police Station | 0.96 | 0.87 | 0.8
|  |  | Fire Station | 0.71 | 0.67 | 0.53
|  |  | Post Office | 0.87 | 0.87 | 0.67
|  |  | Religious Building | 1.05 | 1 | 0.94
|  |  | Retail | 1.4 | 1.26 | 1.06
|  |  | School/University | 0.99 | 0.87 | 0.81
|  |  | Sports Arena | 0.78 | 0.91 | 0.87
|  |  | Town Hall | 0.92 | 0.89 | 0.8
|  |  | Transportation | 0.77 | 0.7 | 0.61
|  |  | Warehouse | 0.66 | 0.66 | 0.48
|  |  | Workshop | 1.2 | 1.19 | 0.9
Space-by-Space Method, Common Space Types - Lighting Power Densities
|  | (Space with Multiple Functions Shall Be Brokenup into Smaller Subspaces) |  | w/sf / RCR Threshold | w/sf / RCR Threshold in Table 9.6.1 | w/sf / RCR Threshold in Table 9.6.1
Atrium - First Three Floors
Atrium - Each Additional Floor
|  |  | Atrium - First 40' in Height | 0.03 per ft (height) / NA
|  |  | Atrium - Height Above 40' | 0.02 per ft (height) / NA
|  |  | Atrium <20' in height |  | 0.03 per ft (height) / NA | 0.03 per ft (height) / NA
|  |  | Atrium ≥20' and ≤40' |  | 0.03 per ft (height) / NA | 0.03 per ft (height) / NA
|  |  | Atrium >40' in height |  | 0.40 + 0.02 per ft (total height) / NA | 0.40 + 0.02 per ft (total height) / NA
|  |  | All Other Audience/Seating Areas |  | 0.43 / 4 | 0.43 / 4
|  |  | Audience/Seating Area (Permanent) for Auditorium | 0.79 / 6 | 0.63 / 6 | 0.63 / 6
|  |  | Audience Seating Area in Convention Center | 0.82 / 4 | 0.82 / 4 | 0.82 / 4
|  |  | Audience Seating Area in Gymnasium | 0.43 / 6 | 0.65 / 6 | 0.65 / 6
|  |  | Audience/Seating Area (Permanent) for Performing Arts Theater | 2.43 / 8 | 2.43 / 8 | 2.03 / 8
|  |  | Audience/Seating Area (Permanent) for Motion Picture Theater | 1.14 / 4 | 1.14 / 4 | 1.14 / 4
|  |  | Audience Seating Area in Religious Building | 1.53 / 4 | 1.53 / 4 | 1.53 / 4
|  |  | Audience Seating Area in Sports Arena | 0.43 / 4 | 0.43 / 4 | 0.43 / 4
|  |  | Classroom/Lecture/Training | 1.24 / 4
|  |  | Audience Seating Area in Penitentiary | 0.43 / 4 | 0.28 / 4 | 0.28 / 4
|  |  | Banking Activity Area | 1.38 / 6 | 1.01 / 6 | 0.86 / 6
|  |  | Classroom/Lecture Halls/Training Rooms in Penitenitary | 1.34 / 4 | 1.34 / 4 | 1.34 / 4
|  |  | All Other Classroom/Lecture Halls/Training Rooms |  | 1.24 / 4 | 0.92 / 4
|  |  | Conference/Meeting/ Multipurpose | 1.23 / 6 | 1.23 / 6 | 1.07 / 6
|  |  | Confinement Cells | 1.10 / 6 | 0.81 / 6 | 0.81 / 6
|  |  | Copy/Print Room |  | 0.72 / 6 | 0.56 / 6
|  |  | Corridor in Facility for Visually Impaired |  | 0.92 / Width <8 ft | 0.92 / Width <8 ft
|  |  | Corridor in Hospital/Healthcare | 0.89 / Width <8 ft | 0.99 / Width <8 ft | 0.92 / Width <8 ft
|  |  | Corridor in Manufacturing Facility | 0.41 / Width <8 ft | 0.41 / Width <8 ft | 0.29 / Width <8 ft
|  |  | All Other Corridor/Transition | 0.66 / Width <8 ft | 0.66 / Width <8 ft | 0.66 / Width <8 ft
|  |  | Courtroom | 1.72 / 6 | 1.72 / 6 | 1.39 / 6
|  |  | Computer Room |  | 1.71 / 4 | 1.33 / 4
|  |  | Dining Area in Penitentiary |  | 0.96 / 6 | 0.96 / 6
|  |  | Dining Area in Facility for Visually Impaired |  | 2.65 / 4 | 2.00 / 4
|  |  | All Other Dining Area | 0.65 / 4 | 0.65 / 4 | 0.63 / 4
|  |  | Dining Area for Bar Lounge/Leisure Dining | 1.31 / 4 | 1.07 / 4 | 0.93 / 4
|  |  | Dining Area for Cafeteria or Fast Food |  | 0.65 / 4 | 0.63 / 4
|  |  | Dining Area for Family Dining | 0.89 / 4 | 0.89 / 4 | 0.71 / 4
|  |  | Dressing/Fitting Room for Performing Arts Theater | 0.40 / 6
|  |  | Electrical/Mechanical Room | 0.95 / 6 | 0.42 / 6 | 0.43 / 6
|  |  | Emergency Vehicle Garage | 0.56 / 4 | 0.56 / 4 | 0.41 / 4
|  |  | Food Preparation | 0.99 / 6 | 1.21 / 6 | 1.06 / 6
|  |  | Guest Room |  | 0.91 / 6 | 0.77 / 6
|  |  | Laboratory in or as Classrooms | 1.28 / 6 | 1.43 / 6 | 1.20 / 6
|  |  | All OtherLaboratories | 1.81 / 6 | 1.81 / 6 | 1.45 / 6
|  |  | Laundry/Washing Area |  | 0.60 / 4 | 0.43 / 4
|  |  | Loading Dock, Interior |  | 0.47 / 6 | 0.58 / 6
|  |  | All Other Lobby | 0.90 / 4 | 0.90 / 4 | 1.00 / 4
|  |  | Lobby in Facility for Visually Impaired |  | 1.80 / 4 | 2.03 / 4
|  |  | Lobby for Elevator | 0.64 / 6 | 0.64 / 6 | 0.69 / 6
|  |  | Lobby in Hotel | 1.06 / 4 | 1.06 / 4 | 1.06 / 4
|  |  | Lobby for Performing Arts Theater | 2.00 / 6 | 2.00 / 6 | 1.70 / 6
|  |  | Lobby for Motion Picture Theater | 0.52 / 4 | 0.59 / 4 | 0.45 / 4
|  |  | Locker Room | 0.75 / 6 | 0.75 / 6 | 0.48 / 6
|  |  | Lounge/Breakroom for Healthcare Facility |  | 0.92 / 6 | 0.78 / 6
|  |  | Lounge/Breakroom (Recreation) | 0.73 / 4 | 0.73 / 4 | 0.62 / 4
|  |  | Office - Enclosed ≤250 sq ft | 1.11 / 8 | 1.11 / 8 | 0.93 / 8
|  |  | Office - Enclosed >250 sq ft | 1.11 / 8 | 1.11 / 8 | 0.93 / 8
|  |  | Office - Open Plan | 0.98 / 4 | 0.98 / 4 | 0.81 / 4
|  |  | Parking Area, Interior | 0.19 / 4 | 0.19 / 4 | 0.14 / 4
|  |  | Pharmacy Area |  | 1.68 / 6 | 1.34 / 6
|  |  | Restrooms in Facility for Visually Impaired |  | 1.21 / 8 | 0.96 / 8
|  |  | All Other Restrooms | 0.98 / 8 | 0.98 / 8 | 0.85 / 8
|  |  | Sales Area (for Accent Lighting See Additional Interior Lighting) | 1.68 / 6 | 1.44 / 6 | 1.22 / 6
|  |  | Seating Area, General |  | 0.54 / 4 | 0.42 / 4
|  |  | Stairway | 0.69 / 10 | Use space LPD containing stairway | Use space LPD containing stairway
|  |  | Stairwell |  | 0.69 / 10 | 0.58 / 10
|  |  | Storage Room <50 sq ft |  | 1.24 / 6 | 0.97 / 10
|  |  | Storage Room ≥50 & ≤1,000 sq ft |  | 0.63 / 6 | 0.46 / 6
|  |  | All Other Storage Room | 0.63 / 6 | 0.63 / 6 | 0.46 / 6
|  |  | Vehicular Maintenance Area | 0.67 / 4 | 0.67 / 4 | 0.56 / 4
|  |  | Workshop | 1.59 / 6 | 1.59 / 6 | 1.14 / 6
|  | Space-by-Space Method, Building-Specific Space Types - Lighting Power Densities |  | w/sf / RCR Threshold | w/sf / RCR Threshold | w/sf / RCR Threshold
|  |  | Chapel in Facility for Visually Impaired |  | 2.21 / 4 | 2.21 / 4
|  |  | Recreation Room /Common Living Rom in Facility for Visually Impaired |  | 2.41 / 6 | 1.80 / 6
|  |  | Convention Center - Exhibit Space | 1.45 / 4 | 1.45 / 4 | 0.88 / 4
|  |  | Dormitory - Living Quarters | 0.38 / 8 | 0.38 / 8 | 0.54 / 8
|  |  | Fire Station - Sleeping Quarters | 0.25 / 6 | 0.22 / 6 | 0.20 / 6
|  |  | Courthouse/Police Station/ Penitentiary - Judges' Chambers | 1.17 / 8
|  |  | Courthouse/Police Station/ Penitentiary - Penitentiary Dining | 1.07 / 6
|  |  | Gymnasium/Fitness Center - Fitness(Exercise) Area | 0.72 / 4 | 0.72 / 4 | 0.50 / 4
|  |  | Gymnasium/Fitness Center - Playing Area | 1.2 / 4 | 1.20 / 4 | 0.82 / 4
|  |  | Hospital - Emergency | 2.26 / 6
|  |  | Hospital/Healthcare - Exam/Treatment | 1.66 / 8 | 1.66 / 8 | 1.68 / 8
|  |  | Hospital/Healthcare - Imaging Room |  | 1.51 / 6 | 1.06 / 6
|  |  | Hospital - Laundry/Washing | 0.60 / 4
|  |  | Hospital - Lounge/Recreation | 1.07 / 6
|  |  | Hospital - Medical Supply | 1.27 / 6 | 0.74 / 6 | 0.54 / 6
|  |  | Hospital/Healthcare - Nursery | 0.88 / 6 | 0.88 / 6 | 1.00 / 6
|  |  | Hospital/Healthcare - Nurses' Station | 0.87 / 6 | 0.71 / 6 | 0.81 / 6
|  |  | Hospital/Healthcare - Operating Room | 1.89 / 6 | 2.48 / 6 | 2.17 / 6
|  |  | Hospital/Healthcare - Patient Room | 0.62 / 6 | 0.62 / 6 | 0.62 / 6
|  |  | Hospital - Pharmacy | 1.14 / 6
|  |  | Hospital/Hospital - Physical Therapy | 0.91 / 6 | 0.91 / 6 | 0.84 / 6
|  |  | Hospital - RadiologyImaging | 1.32 / 6
|  |  | Hospital/Healthcare - Recovery | 1.15 / 6 | 1.15 / 6 | 1.03 / 6
|  |  | Hotel - Dining | 0.82 / 4
|  |  | Hotel - Guest Rooms | 1.11 / 6
|  |  | Highway Lodging - Dining | 0.88 / 4
|  |  | Highway Lodging - Guest Rooms | 0.75 / 6
|  |  | Library - Card File and Cataloging | 0.72 / 4
|  |  | Library - Reading Areas | 0.93 / 4 | 1.06 / 4 | 0.82 / 4
|  |  | Library - Stacks | 1.71 / 4 | 1.71 / 4 | 1.20 / 4
|  |  | Manufacturing - Detailed Manufacturing | 1.29 / 4 | 1.29 / 4 | 0.93 / 4
|  |  | Manufacturing - Equipment Room | 0.95 / 6 | 0.74 / 6 | 0.65 / 6
|  |  | Manufacturing - Extra High Bay (>50 ft Floor to Ceiling Height) | 1.05 / 4 | 1.05 / 4 | 1.05 / 4
|  |  | Manufacturing - High Bay (25-50 ft Floor to Ceiling Height) | 1.23 / 4 | 1.23 / 4 | 0.75 / 4
|  |  | Manufacturing - Low Bay (<25 ft Floor to Ceiling Height) | 1.19 / 4 | 1.19 / 4 | 0.96 / 4
|  |  | Museum - General Exhibition | 1.05 / 6 | 1.05 / 6 | 1.05 / 6
|  |  | Museum - Restoration | 1.02 / 6 | 1.02 / 6 | 0.85 / 6
|  |  | Dressing Room in Performing Arts Theater |  | 0.61 / 6 | 0.36 / 6
|  |  | Post Office - Sorting Area | 0.94 / 4 | 0.94 / 4 | 0.68 / 4
|  |  | Religious Buildings - Fellowship Hall | 0.64 / 4 | 0.64 / 4 | 0.55 / 4
|  |  | Religious Buildings - Worship-Pulpit, Choir | 1.53 / 4 | 1.53 / 4 | 1.53 / 4
|  |  | Retail - Dressing/Fitting Room | 0.87 / 8 | 0.71 / 8 | 0.5 / 8
|  |  | Retail - Mall Concourse | 1.10 / 4 | 1.10 / 4 | 0.9 / 4
|  |  | Sports Arena - Playing Area - Class 4 | 0.72 / 4 | 1.20 / 4 | 1.13 / 4
|  |  | Sports Arena - Playing Area - Class 3 | 1.20 / 4 | 1.80 / 4 | 1.70 / 4
|  |  | Sports Arena - Playing Area - Class 2 | 1.92 / 4 | 2.40 / 4 | 1.96 / 4
|  |  | Sports Arena - Playing Area - Class 1 | 3.01 / 4 | 3.68 / 4 | 2.47 / 4
|  |  | Sports Arena - Ring Sports Arena | 2.68 / 4
|  |  | Transportation - Air/Train/Bus Baggage Area | 0.76 / 4 | 0.53 / 4 | 0.45 / 4
|  |  | Transportation - Airport Concourse | 0.36 / 4 | 0.36 / 4 | 0.31 / 4
|  |  | Transportation - Audience Seating | 0.54 / 4
|  |  | Transportation - Terminal Ticket Counter | 1.08 / 4 | 0.80 / 4 | 0.62 / 4
|  |  | Warehouce - Smaller / Fine Material Storage | 0.95 / 6 | 0.95 / 6 | 0.69 / 6
|  |  | Warehouse - Medium/Bulky Material Storage | 0.58 / 4 | 0.58 / 4 | 0.35 / 4
Additional Interior Lighting Power When Using Space-by-Space Method
|  |  |  | Only IF Specified Lighting Is Installed, and | For specified lighting function and not for any other purpose | For specified lighting function and not for any other purpose
|  |  |  | Automatically Controlled Separately from General Lighting, and | Automatically controlled separately from general lighting, and | Automatically controlled separately from general lighting, and
|  |  |  | To Be Turned Off During Nonbusiness Hours | Turn off during nonbusiness hours | Turn off during nonbusiness hours
|  |  | Decorative Lighting in Addition to General Lighting | Up To 1.0 w/sf for Decorative Appearance or for Highlighting Art or Exhibits | ≤1.0 w/sf for decorative appearance or for highlighting art or exhibits | ≤1.0 w/sf for decorative appearance or for highlighting art or exhibits
|  |  | Lighting Designed and Directed to Highlight Merchandise in Retail Spaces (Sales Areas) | Additional ILPA = | Additional ILPA = | Additional ILPA =
|  |  |  | 1000 W + | 1000 W + | 1000 W +
|  |  |  | (Reatil Area 1 x 0.60 w/sf) + | (Reatil Area 1 x 0.60 w/sf) + | (Reatil Area 1 x 0.45 w/sf) +
|  |  |  | (Retail Area 2 x 0.60 w/sf) + | (Retail Area 2 x 0.60 w/sf) + | (Retail Area 2 x 0.45 w/sf) +
|  |  |  | (Retail Area 3 x 1.40 w/sf) + | (Retail Area 3 x 1.40 w/sf) + | (Retail Area 3 x 1.05 w/sf) +
|  |  |  | (RetailArea 4 x 2.50 w/sf) | (RetailArea 4 x 2.50 w/sf) | (RetailArea 4 x 1.88 w/sf)
|  |  | Room Geometry Adjustment | Allowed for Individual Spaces Where Empty Room RCR Is Greater Than Threshold, LPD Increase = Base Space LPD x 0.20 | Allowed for individual spaces where empty room RCR is >threshold, LPD increase = base space LPD x 0.20 | Allowed for individual spaces where empty room RCR is >threshold, LPD increase = base space LPD x 0.20
Additional Interior Lighting Power When Using Space-by-Space Method And Nonmandatory Controls
|  |  |  | Allowed To Be Used Anywhere in Building When Additional Controls are used as Indicated Provided All Mandatory Controls Are Used | Allowed when using space-by-space method and when all mandatory controls are used | Allowed when using space-by-space method and when all mandatory controls are used
|  |  |  | * Only Used If Requirements For Occupancy Sensors Are Met | * Limited to workstation-specific luminaires | * Limited to workstation-specific luminaires
|  |  |  | ** Cannot Be Used To Satisfy Exemption | ** Occupant allowed to select preferred light level | ** Occupant allowed to select preferred light level
[5 empty] | *** Cannot be used to satisfy exemption | *** Cannot be used to satisfy exemption
|  |  |  | Control Factors | Control Factors | Control Factors
Manual, Continuous Dimming Controls or Programmable Multi-Level Dimming Control
|  |  | Open Office, Private Office | 0.05 | 0.05 | 0.05
|  |  | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.10* | 0.1 | 0.1
|  |  | Retail Sales Area | 0.1 | 0.1 | 0.1
|  |  | Lobby, Atrium, Dining Area, Corridors/Stairways, Gym, Pool Mall Concourse, Parking Garage | 0 | 0 | 0
Programmable Multi-Level Dimming Control Using Programmable Time Scheduling
|  |  | Open Office, Private Office | 0.05 | 0.05 | 0.05
|  |  | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.10* | 0.1 | 0.1
|  |  | Retail Sales Area | 0.1 | 0.1 | 0.1
|  |  | Lobby, Atrium, Dining Area, Corridors/Stairways, Gym, Pool Mall Concourse, Parking Garage | 0.1 | 0.1 | 0.1
Multi-Level Occupancy Sensors
|  |  | Open Office, Private Office | 0.05
|  |  | Conference Room, Meeting Room, Classroom (Lecture/Training) | 0.05
|  |  | Retail Sales Area | 0
|  |  | Lobby, Atrium, Dining Area, Corridors/Stairways, Gym, Pool Mall Concourse, Parking Garage | 0
|  | Occupancy Sensors Controlling Downlight Component of Workstation Specific Luminaires with Continuous Dimming to Off Capabilities in Open Office |  | 0.25 | 0.25* | 0.25*
|  | Occupancy Sensors Controlling Downlight Component of Workstation Specific Luminaires with Continuous Dimming to Off Capabilities In Combination with Personal Continuous Dimming Control of Downlight Illumination by Workstation Occupant in Open Office |  | 0.3 | 0.30* ** | 0.30* **
Automatic Continuous Dimming in Secondary Sidelighted Areas
|  |  | Open Office, Private Office |  | 0.10*** | 0.10***
|  |  | Conference Room, Meeting Room, Classroom (Lecture/Training) |  | 0.10*** | 0.10***
|  |  | Retail Sales Area |  | 0.10*** | 0.10***
|  |  | Lobby, Atrium, Dining Area, Corridors/Stairways, Gym, Pool Mall Concourse, Parking Garage |  | 0.10*** | 0.10***
|  | Automatic Bi-Level or Multi-Level Switching in Primary Sidelighted Areas When Sidelighting Effective Aperture >0.15 - Retail Sales |  | 0.10**
|  | Automatic Bi-Level or Multi-Level Switching in Primary Sidelighted Areas When Sidelighting Effective aperture >0.15 and When Primary Sidelighted Area <250 sq ft |  | 0.10**
|  | Automatic Continuous Daylight Dimming in Primary Sidelighted Area When Sidelighting Effective Aperature >0.15 and When Primary Sidelighted Area <250 sq ft |  | 0.20**
|  | Automatic Continuous Daylight Dimming in Primary Sidelighted Area When Sidelighting Effective Aperature >0.15 and When Primary Sidelighted Area >250 sq ft |  | 0.10**
|  | Automatic Continuous Daylight Dimming in Secondary Sidelighted Areas When Sidelighting Effective Aperture >0.3 |  | 0.10**
|  | Automatic Continuous Daylight Dimming in Daylighted Areas Under Skylights When Total Area <900 sq ft and When Skylight Effective Aperture >0.01 |  | 0.2
|  | Automatic Continuous Daylight Dimming in Daylighted Areas Under Skylights When Total Area >900 sq ft and When Skylight Effective Aperture >0.01 |  | 0.1
Exterior Building Lighting Power
Lighting Power Limits for Building Exteriors
| Zone 0: Undeveloped Area Within National Parks, State Parks, Forest Land, Rural Areas and Other Undeveloped Areas Defined by Authority Having Jurisdiction |  |  | No Tradable Surface Allowance and Single Luminaire ≤60 watts May Be Installed for Each Roadway/Parking Entry, Trail Head, Toilet Facility, or Approved Other Loaction | Single luminaire ≤60 W may be installed for each roadway/parking entry, trail head, and toilet facility, or other location approved by authority having jurisdiction | Single luminaire ≤25 W may be installed for each roadway/parking entry, trail head, and toilet facility, or other location approved by authority having jurisdiction
Zone 1: Developed Areas of National Parks, State Parks, Forest Land and Rural Areas
Zone 1: Tradable Surfaces
|  |  | Base Site Allowance | 500 w | 500 w | 350 w
|  |  | Uncovered Parking Areas and Drives | 0.04 w/sf | 0.04 w/sf | 0.03 w/sf
|  |  | Walkways <10 ft Wide | 0.7 w/lin ft | 0.7 w/lin ft | 0.5 w/lin ft
|  |  | Walkways ≥10 ft Wide, Plaza Areas, Special Feature Areas | 0.14 w/sf | 0.14 w/sf | 0.10 w/sf
|  |  | Dining Areas |  |  | 0.65 w/sf
|  |  | Building Grounds Stairways | 0.75 w/sf | 0.75 w/sf | 0.60 w/sf
|  |  | Pedestrian Tunnels | 0.15 w/sf | 0.15 w/sf | 0.12 w/sf
|  |  | Landscaping | 0.04 w/sf | 0.04 w/sf | 0.03 w/sf
|  |  | Main Building Entries | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Other Doors | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Pedestrian & Vehicular Entrance & Exits |  |  | 14 w/lin ft of Door Width
|  |  | Building Entry Canopies | 0.25 w/sf | 0.25 w/sf | 0.20 w/sf
|  |  | Loading docks |  | 0.50 w/sf | 0.35 w/sf
|  |  | Sales Canopies (Freestanding and Attached) | 0.60 w/sf | 0.60 w/sf | 0.40 w/sf
|  |  | Outdoor Open Sales Areas | 0.25 w/sf | 0.25 w/sf | 0.2.2 w/sf
|  |  | Street Frontage for Vehicle Sales Lots in Addition to "Open Area" Allowance | No Allowance | No Allowance | No Allowance
Zone 1: Non-Tradable Surfaces
|  |  | Building Facades | No Allowance | No Allowance | No Allowance
|  |  | Automated Teller Machines & Night Depositories | 270 w per Location Plus 90 w per Additional ATM per Location | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Entrance & Gatehouse Inspection Stations at Guarded Facilities | 0.75 w/sf of Covered & Uncovered Area | 0.75 w/sf of covered & uncovered area | 0.50 w/sf of covered & uncovered area
|  |  | Loading Areas for Law Enforcement, Fire, Ambulance & other Emergency Service Vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.5 w/sf of covered & uncovered area | 0.35 w/sf of covered & uncovered area
|  |  | Drive-Up Windows/Doors | 400 w per Drive-Through | 400 w per drive-through | 200 w per drive-through
|  |  | Parking Near 24-Hour Retail Entrances | 800 w per Main Entry | 800 w per main entry | 400 w per main entry
Zone 2: Areas Predominantly Consisting of Residential Zoning, Neighborhood Business Districts, Light Industrial with Limited Night-Time Use & Residential Mixed Use Areas
Zone 2: Tradable Surfaces
|  |  | Base Site Allowance | 600 w | 600 w | 400 w
|  |  | Uncovered Parking Areas and Drives | 0.06 w/sf | 0.06 w/sf | 0.04 w/sf
|  |  | Walkways <10 ft Wide | 0.7 w/lin ft | 0.7 w/lin ft | 0.5 w/lin ft
|  |  | Walkways ≥10 ft Wide, Plaza Areas, Special Feature Areas | 0.14 w/sf | 0.14 w/sf | 0.10 w/sf
|  |  | Dining Areas |  |  | 0.65 w/sf
|  |  | Building Grounds Stairways | 1.0 w/sf | 1.0 w/sf | 0.70 w/sf
|  |  | Pedestrian Tunnels | 0.15 w/sf | 0.15 w/sf | 0.12 w/sf
|  |  | Landscaping | 0.05 w/sf | 0.05 w/sf | 0.04 w/sf
|  |  | Main Building Entries | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Other Doors | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Pedestrian & Vehicular Entrance & Exits |  |  | 14 w/lin ft of Door Width
|  |  | Building Entry Canopies | 0.25 w/sf | 0.25 w/sf | 0.25 w/sf
|  |  | Loading docks |  | 0.5 w/sf | 0.35 w/sf
|  |  | Sales Canopies (Freestanding and Attached) | 0.60 w/sf | 0.60 w/sf | 0.40 w/sf
|  |  | Outdoor Open Sales Areas | 0.25 w/sf | 0.25 w/sf | 0.20 w/sf
|  |  | Street Frontage for Vehicle Sales Lots in Addition to "Open Area" Allowance | 10 w/lin ft | 10 w/lin ft | 7 w/lin ft
Zone 2: Non-Tradable Surfaces
|  |  | Building Facades | 0.1 w/sf for Each Illuminated Wall or Surface or 2.5 w/lin ft for Each Illuminated Wall or Surface Length | 0.1 w/sf for Each Illuminated Wall or Surface or 2.5 w/lin ft for Each Illuminated Wall or Surface Length | 0.1 w/sf for Each Illuminated Wall or Surface or 2.5 w/lin ft for Each Illuminated Wall or Surface Length
|  |  | Automated Teller Machines & Night Depositories | 270 w per Location Plus 90 w per Additional ATM per Location | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Entrance & Gatehouse Inspection Stations at Guarded Facilities | 0.75 w/sf of Covered & Uncovered Area | 0.75 w/sf of covered & uncovered area | 0.50 w/sf of covered & uncovered area
|  |  | Loading Areas for Law Enforcement, Fire, Ambulance & other Emergency Service Vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.5 w/sf of Covered & Uncovered Area | 0.35 w/sf of Covered & Uncovered Area
|  |  | Drive-Up Windows/Doors | 400 w per Drive-Through | 400 w per drive-through | 200 w per drive-through
|  |  | Parking Near 24-Hour Retail Entrances | 800 w per Main Entry | 800 w per main entry | 400 w per main entry
Zone 3: All Other Areas
Zone 3: Tradable Surfaces
|  |  | Base Site Allowance | 750 w | 750 w | 500 w
|  |  | Uncovered Parking Areas and Drives | 0.10 w/sf | 0.10 w/sf | 0.06 w/sf
|  |  | Walkways <10 ft Wide | 0.8 w/lin ft | 0.8 w/lin ft | 0.6 w/lin ft
|  |  | Walkways ≥10 ft Wide, Plaza Areas, Special Feature Areas | 0.16 w/sf | 0.16 w/sf | 0.11 w/sf
|  |  | Dining Areas |  |  | 0.75 w/sf
|  |  | Building Grounds Stairways | 1.0 w/sf | 1.0 w/sf | 0.7 w/sf
|  |  | Pedestrian Tunnels | 0.2 w/sf | 0.2 w/sf | 0.14 w/sf
|  |  | Landscaping | 0.05 w/sf | 0.05 w/sf | 0.04 w/sf
|  |  | Main Building Entries | 30 w/lin ft of Door Width | 30 w/lin ft of Door Width
|  |  | Other Doors | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Pedestrian & Vehicular Entrance & Exits |  |  | 21 w/lin ft of Door Width
|  |  | Building Entry Canopies | 0.4 w/sf | 0.4 w/sf | 0.4 w/sf
|  |  | Loading docks |  | 0.50 w/sf | 0.35 w/sf
|  |  | Sales Canopies (Freestanding and Attached) | 0.8 w/sf | 0.8 w/sf | 0.6 w/sf
|  |  | Outdoor Open Sales Areas | 0.5 w/sf | 0.5 w/sf | 0.35 w/sf
|  |  | Street Frontage for Vehicle Sales Lots in Addition to "Open Area" Allowance | 10 w/lin ft | 10 w/lin ft | 7 w/lin ft
Zone 3: Non-Tradable Surfaces
|  |  | Building Facades | 0.15 w/sf for Each Illuminated Wall or Surface or 3.75 w/lin ft for Each Illuminated Wall or Surface Length | 0.15 w/sf for Each Illuminated Wall or Surface or 3.75 w/lin ft for Each Illuminated Wall or Surface Length | 0.15 w/sf for Each Illuminated Wall or Surface or 3.75 w/lin ft for Each Illuminated Wall or Surface Length
|  |  | Automated Teller Machines & Night Depositories | 270 w per Location Plus 90 w per Additional ATM per Location | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Entrance & Gatehouse Inspection Stations at Guarded Facilities | 0.75 w/sf of Covered & Uncovered Area | 0.75 w/sf of covered & uncovered area | 0.50 w/sf of covered & uncovered area
|  |  | Loading Areas for Law Enforcement, Fire, Ambulance & other Emergency Service Vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.5 w/sf of covered & uncovered area | 0.35 w/sf of covered & uncovered area
|  |  | Drive-Up Windows/Doors | 400 w per Drive-Through | 400 w per drive-through | 200 w per drive-through
|  |  | Parking Near 24-Hour Retail Entrances | 800 w per Main Entry | 800 w per main entry | 400 w per main entry
Zone 4: High Activity Commercial Districts in Major Metropolitan Areas as Designated by the Local Jurisdiction
Zone 4: Tradable Surfaces
|  |  | Base Site Allowance | 1300 w | 1300 w | 900 w
|  |  | Uncovered Parking Areas and Drives | 0.13 w/sf | 0.13 w/sf | 0.08 w/sf
|  |  | Walkways <10 ft Wide | 1.0 w/lin ft | 1.0 w/lin ft | 0.7 w/lin ft
|  |  | Walkways ≥10 ft Wide, Plaza Areas, Special Feature Areas | 0.2 w/sf | 0.2 w/sf | 0.14 w/sf
|  |  | Dining Areas |  |  | 0.95 w/sf
|  |  | Building Grounds Stairways | 1.0 w/sf | 1.0 w/sf | 0.70 w/sf
|  |  | Pedestrian Tunnels | 0.3 w/sf | 0.3 w/sf | 0.21 w/sf
|  |  | Landscaping | 0.05 w/sf | 0.05 w/sf | 0.04 w/sf
|  |  | Main Building Entries | 30 w/lin ft of Door Width | 30 w/lin ft of Door Width
|  |  | Other Doors | 20 w/lin ft of Door Width | 20 w/lin ft of Door Width
|  |  | Pedestrian & Vehicular Entrance & Exits |  |  | 21 w/lin ft of Door Width
|  |  | Building Entry Canopies | 0.4 w/sf | 0.4 w/sf | 0.4 w/sf
|  |  | Loading docks |  | 0.5 w/sf | 0.35 w/sf
|  |  | Sales Canopies (Freestanding and Attached) | 1.0 w/sf | 1.0 w/sf | 0.7 w/sf
|  |  | Outdoor Open Sales Areas | 7 w/sf | 0.7 w/sf | 0.5 w/sf
|  |  | Street Frontage for Vehicle Sales Lots in Addition to "Open Area" Allowance | 30 w/lin ft | 30 w/lin ft | 21 w/lin ft
Zone 4: Non-Tradable Surfaces
|  |  | Building Facades | 0.2 w/sf for Each Illuminated Wall or Surface or 5.0 w/lin ft for Each Illuminated Wall or Surface Length | 0.2 w/sf for Each Illuminated Wall or Surface or 5.0 w/lin ft for Each Illuminated Wall or Surface Length | 0.2 w/sf for Each Illuminated Wall or Surface or 5.0 w/lin ft for Each Illuminated Wall or Surface Length
|  |  | Automated Teller Machines & Night Depositories | 270 w per Location Plus 90 w per Additional ATM per Location | 270 w per location plus 90 w per additional ATM per location | 135 w per location plus 45 w per additional ATM per location
|  |  | Entrance & Gatehouse Inspection Stations at Guarded Facilities | 0.75 w/sf of Covered & Uncovered Area | 0.75 w/sf of covered & uncovered area | 0.50 w/sf of covered & uncovered area
|  |  | Loading Areas for Law Enforcement, Fire, Ambulance & other Emergency Service Vehicles | 0.5 w/sf of Covered & Uncovered Area | 0.5 w/sf of covered & uncovered area | 0.35 w/sf of covered & uncovered area
|  |  | Drive-Up Windows/Doors | 400 w per Drive-Through | 400 w per drive-through | 200 w per drive-through
|  |  | Parking Near 24-Hour Retail Entrances | 800 w per Main Entry | 800 w per main entry | 400 w per main entry
| Lighting systems commissioning and completion requirements |  |  |  | Submittals - Completion Requirements | Submittals - Completion Requirements
|  | Documentation requirements |  |  | Construction documents to require submittal of record drawings within 90 days of system acceptance | Construction documents to require submittal of record drawings within 90 days of system acceptance
[5 empty] | Design documents to identify all luminaires for general lighting located within: | Design documents to identify all luminaires for general lighting located within:
[5 empty] | Daylight areas under skylights | Daylight areas under skylights
[5 empty] | Daylight areas under roof monitors | Daylight areas under roof monitors
[5 empty] | Primary sidelighted areas | Primary sidelighted areas
[5 empty] | Secondary sidelighted areas | Secondary sidelighted areas
|  |  | Drawings |  | Location, luminaire identifier, control and circuiting for each piece of lighting equipment | Location, luminaire identifier, control and circuiting for each piece of lighting equipment
[5 empty] | Identification of all luminaires for general lighting in daylight zones | Identification of all luminaires for general lighting in daylight zones
|  |  | Manuals |  | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls | Submittal data indicating all selected options for each piece of lighting equipment and lighting controls
[5 empty] | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions and recommended relamping/cleaning program | Operation and maintenance manuals for each piece of lighting equipment identifying required routine maintenance actions and recommended relamping/cleaning program
[5 empty] | Inspection and recalibration schedules for all lighting controls | Inspection and recalibration schedules for all lighting controls
[5 empty] | Narrative of how each system is intended to operate including recommended settings | Narrative of how each system is intended to operate including recommended settings
|  | Functional testing |  | Lighting Control Devices and Control Systems (Construction Documents To State Who Will Conduct and Certify) | Control devices & systems tested to ensure control hardware & software are calibrated, adjusted, programmed & in proper working condition | Control devices & systems tested to ensure control hardware & software are calibrated, adjusted, programmed & in proper working condition
|  |  | Occupant sensor controls |  | Certify that sensors have been located and aimed | Certify that sensors have been located and aimed
[5 empty] | Test all sensors for projects with ≤7 sensors | Test all sensors for projects with ≤7 sensors
[5 empty] | For projects with >7 sensors, test each unique combination of sensor type and space geometry | For projects with >7 sensors, test each unique combination of sensor type and space geometry
[5 empty] | Test to verify | Test to verify
[5 empty] | 1) Status indicator operation | 1) Status indicator operation
[5 empty] | 2) Turn off or down to permitted level within required time | 2) Turn off or down to permitted level within required time
[5 empty] | 3) Auto-on to permitted level | 3) Auto-on to permitted level
[5 empty] | 4) Manual-on function | 4) Manual-on function
[5 empty] | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation | 5) Lights are not incorrectly turned on by movement in adjacent area or by HVAC operation
|  |  | Automatic time-switch controls |  | Confirm accurate programming for weekday, weekend and holiday schedules | Confirm accurate programming for weekday, weekend and holiday schedules
[5 empty] | Provide documentation to owner of programming | Provide documentation to owner of programming
[5 empty] | Verify correct time and date | Verify correct time and date
[5 empty] | Verify any battery back-up is installed and energized | Verify any battery back-up is installed and energized
[5 empty] | Verify override time limit ≤2 hours | Verify override time limit ≤2 hours
[5 empty] | Simulate occupied condition | Simulate occupied condition
[5 empty] | 1) All lights operated by respective area control switch | 1) All lights operated by respective area control switch
[5 empty] | 2) Switch only operates lighting in enclosed space in which located | 2) Switch only operates lighting in enclosed space in which located
[5 empty] | Simulate unoccupied condition | Simulate unoccupied condition
[5 empty] | 1) Nonexempt lighting turns off | 1) Nonexempt lighting turns off
[5 empty] | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs | 2) Manual override only allows lights in enclosed space where switch is located to turn on or remain on until next scheduled shutoff occurs
|  |  | Daylight responsive controls |  | Verify devices proper location, calibration and accurate setpoints and threshold light levels | Verify devices proper location, calibration and accurate setpoints and threshold light levels
[5 empty] | Verify lighting load adjustments in response to available daylight | Verify lighting load adjustments in response to available daylight
[5 empty] | Locations of equipment adjustment are readily accessible only to authorized personnel | Locations of equipment adjustment are readily accessible only to authorized personnel
Other Equipment
| Motor - Minimum Nominal Efficiency |  |  | For Design A and | 60 HZ General Purpose Electric Motors (Subtype I) | For NEMA Design A & B Motors and
|  |  |  | Design B Motors |  | IEC Design N Motors
ODP - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77
|  |  | 1.5 | 84 | 84 | 84
|  |  | 2 | 85.5 | 85.5 | 85.5
|  |  | 3 | 85.5 | 85.5 | 85.5
|  |  | 5 | 86.5 | 86.5 | 86.5
|  |  | 7.5 | 88.5 | 88.5 | 88.5
|  |  | 10 | 89.5 | 89.5 | 89.5
|  |  | 15 | 90.2 | 90.2 | 90.2
|  |  | 20 | 91 | 91 | 91
|  |  | 25 | 91.7 | 91.7 | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4
|  |  | 50 | 93 | 93 | 93
|  |  | 60 | 93.6 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6
|  |  | 100 | 93.6 | 93.6 | 93.6
|  |  | 125 | 94.1 | 94.1 | 94.1
|  |  | 150 | 94.1 | 94.1 | 94.1
|  |  | 200 | 95.5 | 95 | 95
|  |  | 250 | 95 | 94.5 | 95
|  |  | 300 | 95.4 | 95 | 95.4
|  |  | 350 | 95.4 | 95 | 95.4
|  |  | 400 | 95.8 | 95.4 | 95.8
|  |  | 450 | 95.8 | 95.8 | 96.2
|  |  | 500 | 95.8 | 95.8 | 96.2
ODP - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91 | 91 | 91
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 93 | 93 | 93
|  |  | 20 | 93 | 93 | 93
|  |  | 25 | 93.6 | 93.6 | 93.6
|  |  | 30 | 94.1 | 94.1 | 94.1
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5
|  |  | 60 | 95 | 95 | 95
|  |  | 75 | 95 | 95 | 95
|  |  | 100 | 95.4 | 95.4 | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8
|  |  | 250 | 95.8 | 95.4 | 95.8
|  |  | 300 | 95.8 | 95.4 | 95.8
|  |  | 350 | 95.8 | 95.4 | 95.8
|  |  | 400 | 95.8 | 95.4 | 95.8
|  |  | 450 | 96.2 | 95.8 | 96.2
|  |  | 500 | 96.2 | 95.8 | 96.2
ODP - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 87.5 | 87.5 | 87.5
|  |  | 3 | 88.5 | 88.5 | 88.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 90.2 | 90.2 | 90.2
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 91.7 | 91.7 | 91.7
|  |  | 20 | 92.4 | 92.4 | 92.4
|  |  | 25 | 93 | 93 | 93
|  |  | 30 | 93.6 | 93.6 | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5
|  |  | 100 | 95 | 95 | 95
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95.4 | 95.4 | 95.4
|  |  | 200 | 95.4 | 95.4 | 95.4
|  |  | 250 | 95.4 | 95.4 | 95.8
|  |  | 300 | 95.4 | 95.4 | 95.8
|  |  | 350 | 95.4 | 95.4 | 95.8
|  |  | 400 | 95.8 | NR | NR
|  |  | 450 | 96.2 | NR | NR
|  |  | 500 | 96.2 | NR | NR
ODP - 900 rpm (hp)
|  |  | 1 |  |  | 75.5
|  |  | 1.5 |  |  | 77
|  |  | 2 |  |  | 86.5
|  |  | 3 |  |  | 87.5
|  |  | 5 |  |  | 88.5
|  |  | 7.5 |  |  | 89.5
|  |  | 10 |  |  | 90.2
|  |  | 15 |  |  | 90.2
|  |  | 20 |  |  | 91
|  |  | 25 |  |  | 91
|  |  | 30 |  |  | 91.7
|  |  | 40 |  |  | 91.7
|  |  | 50 |  |  | 92.4
|  |  | 60 |  |  | 93
|  |  | 75 |  |  | 94.1
|  |  | 100 |  |  | 94.1
|  |  | 125 |  |  | 94.1
|  |  | 150 |  |  | 94.1
|  |  | 200 |  |  | 94.1
|  |  | 250 |  |  | 95
TEFC - 3600 rpm (hp)
|  |  | 1 | 77 | 77 | 77
|  |  | 1.5 | 84 | 84 | 84
|  |  | 2 | 85.5 | 85.5 | 85.5
|  |  | 3 | 86.5 | 86.5 | 86.5
|  |  | 5 | 88.5 | 88.5 | 88.5
|  |  | 7.5 | 89.5 | 89.5 | 89.5
|  |  | 10 | 90.2 | 90.2 | 90.2
|  |  | 15 | 91 | 91 | 91
|  |  | 20 | 91 | 91 | 91
|  |  | 25 | 91.7 | 91.7 | 91.7
|  |  | 30 | 91.7 | 91.7 | 91.7
|  |  | 40 | 92.4 | 92.4 | 92.4
|  |  | 50 | 93 | 93 | 93
|  |  | 60 | 93.6 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6 | 93.6
|  |  | 100 | 94.1 | 94.1 | 94.1
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95 | 95 | 95
|  |  | 200 | 95.4 | 95.4 | 95.4
|  |  | 250 | 95.8 | 95.4 | 95.8
|  |  | 300 | 95.8 | 95.4 | 95.8
|  |  | 350 | 95.8 | 95.4 | 95.8
|  |  | 400 | 95.8 | 95.4 | 95.8
|  |  | 450 | 95.8 | 95.4 | 95.8
|  |  | 500 | 95.8 | 95.4 | 95.8
TEFC - 1800 rpm (hp)
|  |  | 1 | 85.5 | 85.5 | 85.5
|  |  | 1.5 | 86.5 | 86.5 | 86.5
|  |  | 2 | 86.5 | 86.5 | 86.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91.7 | 91.7 | 91.7
|  |  | 10 | 91.7 | 91.7 | 91.7
|  |  | 15 | 92.4 | 92.4 | 92.4
|  |  | 20 | 93 | 93 | 93
|  |  | 25 | 93.6 | 93.6 | 93.6
|  |  | 30 | 93.6 | 93.6 | 93.6
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.5 | 94.5 | 94.5
|  |  | 60 | 95 | 95 | 95
|  |  | 75 | 95.4 | 95.4 | 95.4
|  |  | 100 | 95.4 | 95.4 | 95.4
|  |  | 125 | 95.4 | 95.4 | 95.4
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 96.2 | 96.2 | 96.2
|  |  | 250 | 96.2 | 95 | 96.2
|  |  | 300 | 96.2 | 95.4 | 96.2
|  |  | 350 | 96.2 | 95.4 | 96.2
|  |  | 400 | 96.2 | 95.4 | 96.2
|  |  | 450 | 96.2 | 95.4 | 96.2
|  |  | 500 | 96.2 | 95.8 | 96.2
TEFC - 1200 rpm (hp)
|  |  | 1 | 82.5 | 82.5 | 82.5
|  |  | 1.5 | 87.5 | 87.5 | 87.5
|  |  | 2 | 88.5 | 88.5 | 88.5
|  |  | 3 | 89.5 | 89.5 | 89.5
|  |  | 5 | 89.5 | 89.5 | 89.5
|  |  | 7.5 | 91 | 91 | 91
|  |  | 10 | 91 | 91 | 91
|  |  | 15 | 91.7 | 91.7 | 91.7
|  |  | 20 | 91.7 | 91.7 | 91.7
|  |  | 25 | 93 | 93 | 93
|  |  | 30 | 93 | 93 | 93
|  |  | 40 | 94.1 | 94.1 | 94.1
|  |  | 50 | 94.1 | 94.1 | 94.1
|  |  | 60 | 94.5 | 94.5 | 94.5
|  |  | 75 | 94.5 | 94.5 | 94.5
|  |  | 100 | 95 | 95 | 95
|  |  | 125 | 95 | 95 | 95
|  |  | 150 | 95.8 | 95.8 | 95.8
|  |  | 200 | 95.8 | 95.8 | 95.8
|  |  | 250 | 95.8 | 95 | 95.8
|  |  | 300 | 95.8 | 95 | 95.8
|  |  | 350 | 95.8 | 95 | 95.8
|  |  | 400 | 95.8 | NR | NR
|  |  | 450 | 95.8 | NR | NR
|  |  | 500 | 95.8 | NR | NR
TEFC - 900 rpm (hp)
|  |  | 1 |  |  | 75.5
|  |  | 1.5 |  |  | 78.5
|  |  | 2 |  |  | 84
|  |  | 3 |  |  | 85.5
|  |  | 5 |  |  | 86.5
|  |  | 7.5 |  |  | 86.5
|  |  | 10 |  |  | 89.5
|  |  | 15 |  |  | 89.5
|  |  | 20 |  |  | 90.2
|  |  | 25 |  |  | 90.2
|  |  | 30 |  |  | 91.7
|  |  | 40 |  |  | 91.7
|  |  | 50 |  |  | 92.4
|  |  | 60 |  |  | 92.4
|  |  | 75 |  |  | 93.6
|  |  | 100 |  |  | 93.6
|  |  | 125 |  |  | 94.1
|  |  | 150 |  |  | 94.1
|  |  | 200 |  |  | 94.5
|  |  | 250 |  |  | 95
| Motor - Minimum Nominal Efficiency |  |  |  |  | For NEMA Design C and
IEC Design H Motors
ODP - 1800 rpm (hp)
|  |  | 1 |  |  | 85.5
|  |  | 1.5 |  |  | 86.5
|  |  | 2 |  |  | 86.5
|  |  | 3 |  |  | 89.5
|  |  | 5 |  |  | 89.5
|  |  | 7.5 |  |  | 91
|  |  | 10 |  |  | 91.7
|  |  | 15 |  |  | 93
|  |  | 20 |  |  | 93
|  |  | 25 |  |  | 93.6
|  |  | 30 |  |  | 94.1
|  |  | 40 |  |  | 94.1
|  |  | 50 |  |  | 94.5
|  |  | 60 |  |  | 95
|  |  | 75 |  |  | 95
|  |  | 100 |  |  | 95.4
|  |  | 125 |  |  | 95.4
|  |  | 150 |  |  | 95.8
|  |  | 200 |  |  | 95.8
ODP - 1200 rpm (hp)
|  |  | 1 |  |  | 82.5
|  |  | 1.5 |  |  | 86.5
|  |  | 2 |  |  | 87.5
|  |  | 3 |  |  | 88.5
|  |  | 5 |  |  | 89.5
|  |  | 7.5 |  |  | 90.2
|  |  | 10 |  |  | 91.7
|  |  | 15 |  |  | 91.7
|  |  | 20 |  |  | 92.4
|  |  | 25 |  |  | 93
|  |  | 30 |  |  | 93.6
|  |  | 40 |  |  | 94.1
|  |  | 50 |  |  | 94.1
|  |  | 60 |  |  | 94.5
|  |  | 75 |  |  | 94.5
|  |  | 100 |  |  | 95
|  |  | 125 |  |  | 95
|  |  | 150 |  |  | 95.4
|  |  | 200 |  |  | 95.4
ODP - 900 rpm (hp)
|  |  | 1 |  |  | 75.5
|  |  | 1.5 |  |  | 77
|  |  | 2 |  |  | 86.5
|  |  | 3 |  |  | 87.5
|  |  | 5 |  |  | 88.5
|  |  | 7.5 |  |  | 89.5
|  |  | 10 |  |  | 90.2
|  |  | 15 |  |  | 90.2
|  |  | 20 |  |  | 91
|  |  | 25 |  |  | 91
|  |  | 30 |  |  | 91.7
|  |  | 40 |  |  | 91.7
|  |  | 50 |  |  | 92.4
|  |  | 60 |  |  | 93
|  |  | 75 |  |  | 94.1
|  |  | 100 |  |  | 94.1
|  |  | 125 |  |  | 94.1
|  |  | 150 |  |  | 94.1
|  |  | 200 |  |  | 94.1
TEFC - 1800 rpm (hp)
|  |  | 1 |  |  | 85.5
|  |  | 1.5 |  |  | 86.5
|  |  | 2 |  |  | 86.5
|  |  | 3 |  |  | 89.5
|  |  | 5 |  |  | 89.5
|  |  | 7.5 |  |  | 91.7
|  |  | 10 |  |  | 91.7
|  |  | 15 |  |  | 92.4
|  |  | 20 |  |  | 93
|  |  | 25 |  |  | 93.6
|  |  | 30 |  |  | 93.6
|  |  | 40 |  |  | 94.1
|  |  | 50 |  |  | 94.5
|  |  | 60 |  |  | 95
|  |  | 75 |  |  | 95.4
|  |  | 100 |  |  | 95.4
|  |  | 125 |  |  | 95.4
|  |  | 150 |  |  | 95.8
|  |  | 200 |  |  | 96.2
TEFC - 1200 rpm (hp)
|  |  | 1 |  |  | 82.5
|  |  | 1.5 |  |  | 87.5
|  |  | 2 |  |  | 88.5
|  |  | 3 |  |  | 89.5
|  |  | 5 |  |  | 89.5
|  |  | 7.5 |  |  | 91
|  |  | 10 |  |  | 91
|  |  | 15 |  |  | 91.7
|  |  | 20 |  |  | 91.7
|  |  | 25 |  |  | 93
|  |  | 30 |  |  | 93
|  |  | 40 |  |  | 94.1
|  |  | 50 |  |  | 94.1
|  |  | 60 |  |  | 94.5
|  |  | 75 |  |  | 94.5
|  |  | 100 |  |  | 95
|  |  | 125 |  |  | 95
|  |  | 150 |  |  | 95.8
|  |  | 200 |  |  | 95.8
TEFC - 900 rpm (hp)
|  |  | 1 |  |  | 75.5
|  |  | 1.5 |  |  | 78.5
|  |  | 2 |  |  | 84
|  |  | 3 |  |  | 85.5
|  |  | 5 |  |  | 86.5
|  |  | 7.5 |  |  | 86.5
|  |  | 10 |  |  | 89.5
|  |  | 15 |  |  | 89.5
|  |  | 20 |  |  | 90.2
|  |  | 25 |  |  | 90.2
|  |  | 30 |  |  | 91.7
|  |  | 40 |  |  | 91.7
|  |  | 50 |  |  | 92.4
|  |  | 60 |  |  | 92.4
|  |  | 75 |  |  | 93.6
|  |  | 100 |  |  | 93.6
|  |  | 125 |  |  | 94.1
|  |  | 150 |  |  | 94.1
|  |  | 200 |  |  | 94.5
|  |  |  | General Purpose Electric Motors (Subtype II and Design B) | General Purpose Electric Motors (Subtype II and Design B)
ODP - 3600 rpm (hp)
|  |  | 1 | NR | NR
|  |  | 1.5 | 82.5 | 82.5
|  |  | 2 | 84 | 84
|  |  | 3 | 84 | 84
|  |  | 5 | 85.5 | 85.5
|  |  | 7.5 | 87.5 | 87.5
|  |  | 10 | 88.5 | 88.5
|  |  | 15 | 89.5 | 89.5
|  |  | 20 | 90.2 | 90.2
|  |  | 25 | 91 | 91
|  |  | 30 | 91 | 91
|  |  | 40 | 91.7 | 91.7
|  |  | 50 | 92.4 | 92.4
|  |  | 60 | 93 | 93
|  |  | 75 | 93 | 93
|  |  | 100 | 93 | 93
|  |  | 125 | 93.6 | 93.6
|  |  | 150 | 93.6 | 93.6
|  |  | 200 | 94.5 | 94.5
|  |  | 250 | 94.5 | 94.5
|  |  | 300 | 95 | 95
|  |  | 350 | 95 | 95
|  |  | 400 | 95.4 | 95.4
|  |  | 450 | 95.8 | 95.8
|  |  | 500 | 95.8 | 95.8
ODP - 1800 rpm (hp)
|  |  | 1 | 82.5 | 82.5
|  |  | 1.5 | 84 | 84
|  |  | 2 | 84 | 84
|  |  | 3 | 86.5 | 86.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 88.5 | 88.5
|  |  | 10 | 89.5 | 89.5
|  |  | 15 | 91 | 91
|  |  | 20 | 91 | 91
|  |  | 25 | 91.7 | 91.7
|  |  | 30 | 92.4 | 92.4
|  |  | 40 | 93 | 93
|  |  | 50 | 93 | 93
|  |  | 60 | 93.6 | 93.6
|  |  | 75 | 94.1 | 94.1
|  |  | 100 | 94.1 | 94.1
|  |  | 125 | 94.5 | 94.5
|  |  | 150 | 95 | 95
|  |  | 200 | 95 | 95
|  |  | 250 | 95.4 | 95.4
|  |  | 300 | 95.4 | 95.4
|  |  | 350 | 95.4 | 95.4
|  |  | 400 | 95.4 | 95.4
|  |  | 450 | 95.8 | 95.8
|  |  | 500 | 95.8 | 95.8
ODP - 1200 rpm (hp)
|  |  | 1 | 80 | 80
|  |  | 1.5 | 84 | 84
|  |  | 2 | 85.5 | 85.5
|  |  | 3 | 86.5 | 86.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 88.5 | 88.5
|  |  | 10 | 90.2 | 90.2
|  |  | 15 | 90.2 | 90.2
|  |  | 20 | 91 | 91
|  |  | 25 | 91.7 | 91.7
|  |  | 30 | 92.4 | 92.4
|  |  | 40 | 93 | 93
|  |  | 50 | 93 | 93
|  |  | 60 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6
|  |  | 100 | 94.1 | 94.1
|  |  | 125 | 94.1 | 94.1
|  |  | 150 | 94.5 | 94.5
|  |  | 200 | 94.5 | 94.5
|  |  | 250 | 95.4 | 95.4
|  |  | 300 | 95.4 | 95.4
|  |  | 350 | 95.4 | 95.4
|  |  | 400 | NR | NR
|  |  | 450 | NR | NR
|  |  | 500 | NR | NR
ODP - 900 rpm (hp)
|  |  | 1 | 74 | 74
|  |  | 1.5 | 75.5 | 75.5
|  |  | 2 | 85.5 | 85.5
|  |  | 3 | 86.5 | 86.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 88.5 | 88.5
|  |  | 10 | 89.5 | 89.5
|  |  | 15 | 89.5 | 89.5
|  |  | 20 | 90.2 | 90.2
|  |  | 25 | 90.2 | 90.2
|  |  | 30 | 91 | 91
|  |  | 40 | 91 | 91
|  |  | 50 | 91.7 | 91.7
|  |  | 60 | 92.4 | 92.4
|  |  | 75 | 93.6 | 93.6
|  |  | 100 | 93.6 | 93.6
|  |  | 125 | 93.6 | 93.6
|  |  | 150 | 93.6 | 93.6
|  |  | 200 | 93.6 | 93.6
|  |  | 250 | 94.5 | 94.5
|  |  | 300 | NR | NR
|  |  | 350 | NR | NR
|  |  | 400 | NR | NR
|  |  | 450 | NR | NR
|  |  | 500 | NR | NR
TEFC - 3600 rpm (hp)
|  |  | 1 | 75.5 | 75.5
|  |  | 1.5 | 82.5 | 82.5
|  |  | 2 | 84 | 84
|  |  | 3 | 85.5 | 85.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 88.5 | 88.5
|  |  | 10 | 89.5 | 89.5
|  |  | 15 | 90.2 | 90.2
|  |  | 20 | 90.2 | 90.2
|  |  | 25 | 91 | 91
|  |  | 30 | 91 | 91
|  |  | 40 | 91.7 | 91.7
|  |  | 50 | 92.4 | 92.4
|  |  | 60 | 93 | 93
|  |  | 75 | 93 | 93
|  |  | 100 | 93.6 | 93.6
|  |  | 125 | 94.5 | 94.5
|  |  | 150 | 94.5 | 94.5
|  |  | 200 | 95 | 95
|  |  | 250 | 95.4 | 95.4
|  |  | 300 | 95.4 | 95.4
|  |  | 350 | 95.4 | 95.4
|  |  | 400 | 95.4 | 95.4
|  |  | 450 | 95.4 | 95.4
|  |  | 500 | 95.4 | 95.4
TEFC - 1800 rpm (hp)
|  |  | 1 | 82.5 | 82.5
|  |  | 1.5 | 84 | 84
|  |  | 2 | 84 | 84
|  |  | 3 | 87.5 | 87.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 89.5 | 89.5
|  |  | 10 | 89.5 | 89.5
|  |  | 15 | 91 | 91
|  |  | 20 | 91 | 91
|  |  | 25 | 92.4 | 92.4
|  |  | 30 | 92.4 | 92.4
|  |  | 40 | 93 | 93
|  |  | 50 | 93 | 93
|  |  | 60 | 93.6 | 93.6
|  |  | 75 | 94.1 | 94.1
|  |  | 100 | 94.5 | 94.5
|  |  | 125 | 94.5 | 94.5
|  |  | 150 | 95 | 95
|  |  | 200 | 95 | 95
|  |  | 250 | 95 | 95
|  |  | 300 | 95.4 | 95.4
|  |  | 350 | 95.4 | 95.4
|  |  | 400 | 95.4 | 95.4
|  |  | 450 | 95.4 | 95.4
|  |  | 500 | 95.8 | 95.8
TEFC - 1200 rpm (hp)
|  |  | 1 | 80 | 80
|  |  | 1.5 | 85.5 | 85.5
|  |  | 2 | 86.5 | 86.5
|  |  | 3 | 87.5 | 87.5
|  |  | 5 | 87.5 | 87.5
|  |  | 7.5 | 89.5 | 89.5
|  |  | 10 | 89.5 | 89.5
|  |  | 15 | 90.2 | 90.2
|  |  | 20 | 90.2 | 90.2
|  |  | 25 | 91.7 | 91.7
|  |  | 30 | 91.7 | 91.7
|  |  | 40 | 93 | 93
|  |  | 50 | 93 | 93
|  |  | 60 | 93.6 | 93.6
|  |  | 75 | 93.6 | 93.6
|  |  | 100 | 94.1 | 94.1
|  |  | 125 | 94.1 | 94.1
|  |  | 150 | 95 | 95
|  |  | 200 | 95 | 95
|  |  | 250 | 95 | 95
|  |  | 300 | 95 | 95
|  |  | 350 | 95 | 95
|  |  | 400 | NR | NR
|  |  | 450 | NR | NR
|  |  | 500 | NR | NR
TEFC - 900 rpm (hp)
|  |  | 1 | 74 | 74
|  |  | 1.5 | 77 | 77
|  |  | 2 | 82.5 | 82.5
|  |  | 3 | 84 | 84
|  |  | 5 | 85.5 | 85.5
|  |  | 7.5 | 85.5 | 85.5
|  |  | 10 | 88.5 | 88.5
|  |  | 15 | 88.5 | 88.5
|  |  | 20 | 89.5 | 89.5
|  |  | 25 | 89.5 | 89.5
|  |  | 30 | 91 | 91
|  |  | 40 | 91 | 91
|  |  | 50 | 91.7 | 91.7
|  |  | 60 | 91.7 | 91.7
|  |  | 75 | 93 | 93
|  |  | 100 | 93 | 93
|  |  | 125 | 93.6 | 93.6
|  |  | 150 | 93.6 | 93.6
|  |  | 200 | 94.1 | 94.1
|  |  | 250 | 94.5 | 94.5
|  |  | 300 | NR | NR
|  |  | 350 | NR | NR
|  |  | 400 | NR | NR
|  |  | 450 | NR | NR
|  |  | 500 | NR | NR
[5 empty] | Polyphase Small Electric Motors | Polyphase Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 |  | 65.6 | 65.6
|  |  | 0.33 |  | 69.5 | 69.5
|  |  | 0.5 |  | 73.4 | 73.4
|  |  | 0.75 |  | 76.8 | 76.8
|  |  | 1 |  | 77 | 77
|  |  | 1.5 |  | 84 | 84
|  |  | 2 |  | 85.5 | 85.5
|  |  | 3 |  | 85.5 | 85.5
Open Motor - 1800 rpm (hp)
|  |  | 0.25 |  | 69.5 | 69.5
|  |  | 0.33 |  | 73.4 | 73.4
|  |  | 0.5 |  | 78.2 | 78.2
|  |  | 0.75 |  | 81.1 | 81.1
|  |  | 1 |  | 83.5 | 83.5
|  |  | 1.5 |  | 86.5 | 86.5
|  |  | 2 |  | 86.5 | 86.5
|  |  | 3 |  | 86.9 | 86.9
Open Motor - 1200 rpm (hp)
|  |  | 0.25 |  | 67.5 | 67.5
|  |  | 0.33 |  | 71.4 | 71.4
|  |  | 0.5 |  | 75.3 | 75.3
|  |  | 0.75 |  | 81.7 | 81.7
|  |  | 1 |  | 82.5 | 82.5
|  |  | 1.5 |  | 83.8 | 83.8
|  |  | 2 |  | N/A | N/A
|  |  | 3 |  | N/A | N/A
[5 empty] | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors | Capacitor-Start Capacitor-Run and Capacitor-Start Induction-Run Small Electric Motors
Open Motor - 3600 rpm (hp)
|  |  | 0.25 |  | 66.6 | 66.6
|  |  | 0.33 |  | 70.5 | 70.5
|  |  | 0.5 |  | 72.4 | 72.4
|  |  | 0.75 |  | 76.2 | 76.2
|  |  | 1 |  | 80.4 | 80.4
|  |  | 1.5 |  | 81.5 | 81.5
|  |  | 2 |  | 82.9 | 82.9
|  |  | 3 |  | 84.1 | 84.1
Open Motor - 1800 rpm (hp)
|  |  | 0.25 |  | 69.5 | 68.5
|  |  | 0.33 |  | 72.4 | 72.4
|  |  | 0.5 |  | 76.2 | 76.2
|  |  | 0.75 |  | 81.8 | 81.8
|  |  | 1 |  | 82.6 | 82.6
|  |  | 1.5 |  | 83.8 | 83.8
|  |  | 2 |  | 84.5 | 84.5
|  |  | 3 |  | N/A | N/A
Open Motor - 1200 rpm (hp)
|  |  | 0.25 |  | 67.5 | 62.2
|  |  | 0.33 |  | 71.4 | 66.6
|  |  | 0.5 |  | 75.3 | 76.2
|  |  | 0.75 |  | 81.7 | 80.2
|  |  | 1 |  | 82.5 | 81.1
|  |  | 1.5 |  | 83.8 | N/A
|  |  | 2 |  | N/A | N/A
|  |  | 3 |  | N/A | N/A
| Fire Pump Electric Motor Efficiency |  |  |  | See Table 10.8-6 | See Table 10.8-5
|  |  | 1 to 500 hp |  | Generally lower efficiencies | Generally lower efficiencies
| Service Water Pressure Booster Systems |  |  | Designed Such That | Designed Such That | Designed Such That
|  |  |  | Pressure Sensors Vary Speed or Start/Stop Pumps; | Pressure Sensors Vary Speed or Start/Stop Pumps; | Pressure Sensors Vary Speed or Start/Stop Pumps;
|  |  |  | No Device To Reduce Water Supply Pressure; | No Device To Reduce Water Supply Pressure; | No Device To Reduce Water Supply Pressure;
|  |  |  | No Booster Pump Operation When No Flow | No Booster Pump Operation When No Flow | No Booster Pump Operation When No Flow
Elevators
|  |  | Cab Lighting | ≥35 Lumens per Watt | Sum of lumens divided by sum of watts ≥35 | Sum of lumens divided by sum of watts ≥35
|  |  | Cab Ventilation Power Limitation | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm | ≤0.33 Watts per cfm
|  |  | Cab Standby Mode | Lighting & Ventilation De-energized When Stopped and Unoccupied With Doors Closed for>15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes | Lighting & ventilation de-energized when stopped and unoccupied with doors closed for >15 minutes
Escalators and moving walks
|  |  | Automatic controls |  | To reduce speed to minimum permitted speed when not conveying passengers | To reduce speed to minimum permitted speed when not conveying passengers
Whole-Building Energy Monitoring
Monitoring
|  |  | Measurement device for energy use supplied by utility, energy provider or plant not within building |  | Natural gas | Natural gas
[5 empty] | Fuel oil | Fuel oil
[5 empty] | Propane | Propane
[5 empty] | Steam | Steam
[5 empty] | Chilled water | Chilled water
[5 empty] | Hot water | Hot water
Recording and reporting
|  |  | Recorded |  | At least every 60 minutes | At least every 60 minutes
|  |  | Reported (and with capability to create user reports) |  | Hourly | Hourly
[5 empty] | Daily | Daily
[5 empty] | Monthly | Monthly
[5 empty] | Annually | Annually
|  |  | Retained |  | ≥36 months | ≥36 months
Alternate Compliance
|  |  | Section 11, Energy Cost Budget Method | For code compliance | For code complaince | For code complaince
|  | Appendix G, Performance Rating Method |  | Mandatory for comply with beyond code programs/rating systems | Allowed for code compliance in 2015 excerpt | For code complaince